## About
Cost Breakdown Structure for Wave Energy Device
Created by |  | Mirko Previsic
Company |  | RE Vision Consulting, LLC
Contact |  | mirko@re-vision.net
Date |  | 2012-08-07
Comments/Notes
1. This spreadsheet provides the background and details of the cost and economic assessment of the Wave Energy Device
2. This spreadsheet supports the primary reports on the Wave Energy device
3. Cost Estimates provided herein are based on concept design and engineering data and have high levels of uncertainties embedded
Disclaimer

## Report Tables
Capex and Opex Table Rounding | 0 | # of digits to zero
Cost Basis in $'s | 1000
Total Cost in Thousands ($)
| 1 Unit | 10 Units | 50 Units | 100 Units
| Total Cost | Total Cost | Total Cost | Total Cost
Development | 4553 | 8774 | 11003 | 10820
Infrastructure | 990 | 4860 | 7566 | 17310
Mooring/Foundation | 525 | 4723 | 23615 | 47230
Device Structural Components | 2939 | 20675 | 91548 | 177933
Power Take Off | 623 | 4937 | 21685 | 41284
Subsystem Integration & Profit Margin | 356 | 2561 | 11323 | 21922
Installation | 5909 | 9082 | 21531 | 37860
Contingency | 1590 | 5561 | 18827 | 35436
Total | 17485 | 61173 | 207098 | 389795
Capex and Opex Table Rounding | 1 | # of digits to zero
Capex
| 1 Unit | 10 Units | 50 Units | 100 Units
| $ / kW | $ / kW | $ / kW | $ / kW
Development | 15920 | 3070 | 770 | 380
Infrastructure | 3460 | 1700 | 530 | 610
Mooring/Foundation | 1830 | 1650 | 1650 | 1650
Device Structural Components | 10280 | 7230 | 6400 | 6220
Power Take Off | 2180 | 1730 | 1520 | 1440
Subsystem Integration & Profit Margin | 1250 | 900 | 790 | 770
Installation | 20660 | 3180 | 1510 | 1320
Contingency | 5560 | 1940 | 1320 | 1240
Total | 61140 | 21400 | 14490 | 13630
Capex
| 10 Units |  | 50 Units |  | 100 Units
| cents/kWh | % | cents/kWh | % | cents/kWh | %
Development | 14.0956 | 14.34% | 3.5354 | 5.313% | 1.7383 | 2.776%
Infrastructure | 7.8078 | 7.945% | 2.431 | 3.653% | 2.7809 | 4.441%
Mooring/Foundation | 7.5877 | 7.721% | 7.5877 | 11.4% | 7.5877 | 12.12%
Device Structural Components | 33.215 | 33.8% | 29.4155 | 44.21% | 28.5859 | 45.65%
Power Take Off | 7.9313 | 8.07% | 6.9675 | 10.47% | 6.6325 | 10.59%
Subsystem Integration & Profit Margin | 4.1146 | 4.187% | 3.6383 | 5.468% | 3.5218 | 5.624%
Installation | 14.5907 | 14.85% | 6.9182 | 10.4% | 6.0823 | 9.713%
Contingency | 8.9343 | 9.091% | 6.0494 | 9.091% | 5.693 | 9.091%
Total | 98.277 |  | 66.543 |  | 62.6225
Capex and Opex Table Rounding | 0 | # of digits to zero
Cost Basis in $'s | 1000
Annual Cost in Thousands ($)
| 1 Unit | 10 Units | 50 Units | 100 Units
| Total Cost / yr | Total Cost / yr | Total Cost / yr | Total Cost / yr
Insurance | 227 | 937 | 1773 | 1718
Environmental Monitoring & Regulatory Compliance | 710 | 1121 | 1121 | 1121
Marine Operations | 27 | 266 | 562 | 1125
Shoreside Operations | 142 | 400 | 455 | 675
Replacement Parts | 54 | 491 | 2305 | 3921
Consumables | 8 | 80 | 400 | 800
Total | 1168 | 3295 | 6616 | 9360
Capex and Opex Table Rounding | 1 | # of digits to zero
Opex
| 1 Unit | 10 Units | 50 Units | 100 Units
| $ / kW-yr | $ / kW-yr | $ / kW-yr | $ / kW-yr
Insurance | 790 | 330 | 120 | 60
Environmental Monitoring & Regulatory Compliance | 2480 | 390 | 80 | 40
Marine Operations | 90 | 90 | 40 | 40
Shoreside Operations | 490 | 140 | 30 | 20
Replacement Parts | 190 | 170 | 160 | 140
Consumables | 30 | 30 | 30 | 30
Total | 4070 | 1150 | 460 | 330
Opex
| 10 Units |  | 50 Units |  | 100 Units
| cents/kWh | % | cents/kWh | % | cents/kWh | %
Insurance | 13.3681 | 28.43% | 5.0595 | 26.79% | 2.4513 | 18.35%
Environmental Monitoring & Regulatory Compliance | 15.9975 | 34.02% | 3.1995 | 16.94% | 1.5997 | 11.98%
Marine Operations | 3.7916 | 8.064% | 1.6049 | 8.499% | 1.6049 | 12.02%
Shoreside Operations | 5.7074 | 12.14% | 1.2978 | 6.873% | 0.96275 | 7.209%
Replacement Parts | 7.0114 | 14.91% | 6.5797 | 34.84% | 5.5954 | 41.89%
Consumables | 1.1417 | 2.428% | 1.1417 | 6.046% | 1.1417 | 8.548%
Total | 47.0177 |  | 18.883 |  | 13.3557
Capex & Opex
| 10 Units |  | 50 Units |  | 100 Units
| cents/kWh | % | cents/kWh | % | cents/kWh | %
Device | 52.8486 | 36.37% | 47.609 | 55.73% | 46.328 | 60.98%
Infrastructure | 7.8078 | 5.374% | 2.431 | 2.846% | 2.7809 | 3.66%
Development | 14.0956 | 9.701% | 3.5354 | 4.139% | 1.7383 | 2.288%
Installation | 14.5907 | 10.04% | 6.9182 | 8.098% | 6.0823 | 8.005%
Contingency | 8.9343 | 6.149% | 6.0494 | 7.081% | 5.693 | 7.493%
Operation and Maintenance | 47.0177 | 32.36% | 18.883 | 22.1% | 13.3557 | 17.58%
Total | 145.2946 |  | 85.426 |  | 75.9783

## Report Graphs
# of Units | 1 | 10 | 50 | 100
Installed Capacity (kW) | 286 | 2860 | 14300 | 28600
Installed Capacity (MW) | 0.286 | 2.86 | 14.3 | 28.6
Sensitvity Graphs
Mean Wave Height (m) | Wave Power Density (kW/m) | LCoE - cents/kWh
1.5 | 10.391 | 160.8878
1.7 | 14.4073 | 126.741
1.9 | 19.2621 | 102.5294
2.1 | 25.0144 | 84.7233
2.3 | 31.7209 | 71.236
2.5 | 39.4361 | 60.7686
2.7 | 48.2128 | 52.4776
2.9 | 58.102 | 45.7955
3.1 | 69.1535 | 40.329
Value | 36.5605 | 43.9071 | 51.2538 | 58.6005 | 65.9471 | 73.2938 | 80.6405 | 87.9871 | 95.3338 | 102.6805 | 110.0272 | 117.3738 | 124.7205 | 132.0672 | 139.4138 | 146.7605 | 154.1072 | 161.4538 | 168.8005 | 176.1472
% | 0% | 0% | 3.52% | 16.92% | 35.66% | 55.18% | 70.18% | 80.4% | 87.54% | 92.26% | 95.3% | 97.32% | 98.54% | 99.54% | 99.86% | 100% | 100% | 100% | 100% | 100%
RESULTS
% | Value
10% | 54.8065
50% | 71.3442
90% | 99.1628

## Performance & Economics
Technical Input Parameters | [13 empty] | Resource and Performance Outputs
Note: Inputs shown in green
Power Conversion System Parameters | [13 empty] | Site Resource Parameters
| PTO Efficiency |  |  |  |  | 80% | [8 empty] | Average Hs |  |  | 2.3812 | m
| Rated Power |  |  |  |  | 286 | kW | [7 empty] | Average Te |  |  | 9.2517 | sec
[15 empty] | Average Power Flux |  |  | 33.5011 | kW/m
Array Parameters
| Array/Turbine Availability |  |  |  |  | 95%
| Transmission Efficiency |  |  |  |  | 98%
Energy Extraction
[15 empty] | Average Extracted Power |  |  | 108.3926 | kW
[15 empty] | Average Electric Power |  |  | 85.9212 | kW
[15 empty] | Rated Electric Power |  |  | 286 | kW
[15 empty] | Machine Capacity Factor |  |  | 30.04%
[15 empty] | Annual Output |  |  | 700.7352 | MWh/year
[15 empty] | # of US homes equivalent |  |  | 66.0932
Wave Resource Frequency Distribution (unnormalized)
Te
|  |  |  | 4.5 | 5.5 | 6.5 | 7.5 | 8.5 | 9.5 | 10.5 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5
|  | Hs | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.75 | 0 | 4 | 70 | 101 | 64 | 67 | 30 | 4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 342
|  |  | 1.25 | 2 | 122 | 342 | 461 | 510 | 360 | 182 | 54 | 14 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2049
|  |  | 1.75 | 0 | 122 | 553 | 534 | 513 | 430 | 252 | 141 | 80 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 2633
|  |  | 2.25 | 0 | 30 | 437 | 531 | 454 | 511 | 395 | 186 | 148 | 41 | 4 | 2 | 1 | 0 | 0 | 0 | 2740
|  |  | 2.75 | 0 | 1 | 193 | 314 | 243 | 407 | 409 | 220 | 142 | 47 | 9 | 8 | 0 | 0 | 0 | 0 | 1993
|  |  | 3.25 | 0 | 0 | 15 | 116 | 115 | 245 | 298 | 181 | 101 | 50 | 18 | 5 | 0 | 0 | 0 | 0 | 1144
|  |  | 3.75 | 0 | 0 | 2 | 11 | 29 | 127 | 242 | 189 | 66 | 41 | 28 | 7 | 0 | 0 | 0 | 0 | 742
|  |  | 4.25 | 0 | 0 | 0 | 1 | 6 | 27 | 125 | 160 | 69 | 37 | 19 | 11 | 4 | 0 | 0 | 0 | 459
|  |  | 4.75 | 0 | 0 | 0 | 0 | 2 | 5 | 40 | 55 | 47 | 29 | 16 | 8 | 1 | 0 | 0 | 0 | 203
|  |  | 5.25 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 26 | 32 | 20 | 8 | 3 | 2 | 0 | 0 | 0 | 109
|  |  | 5.75 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 19 | 13 | 18 | 10 | 1 | 1 | 0 | 0 | 0 | 69
|  |  | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 10 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 44
|  |  | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 8
|  |  | 7.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 6
|  |  | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | 8.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1
|  |  | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2
|  |  | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2 | 279 | 1612 | 2069 | 1936 | 2182 | 1998 | 1244 | 725 | 315 | 124 | 49 | 10 | 2 | 0 | 0
Wave Resource Power Flux
Te
|  |  |  | 4.5 | 5.5 | 6.5 | 7.5 | 8.5 | 9.5 | 10.5 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5
|  | Hs | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.75 | 0 | 1.5159 | 1.7916 | 2.0672 | 2.3428 | 2.6184 | 2.8941 | 3.1697 | 0 | 3.7209 | 0 | 4.2722 | 0 | 0 | 0 | 0 | 24.3928
|  |  | 1.25 | 3.4453 | 4.2109 | 4.9766 | 5.7422 | 6.5078 | 7.2734 | 8.0391 | 8.8047 | 9.5703 | 0 | 0 | 0 | 12.6328 | 13.3984 | 0 | 0 | 84.6016
|  |  | 1.75 | 0 | 8.2534 | 9.7541 | 11.2547 | 12.7553 | 14.2559 | 15.7566 | 17.2572 | 18.7578 | 20.2584 | 0 | 0 | 0 | 26.2609 | 0 | 0 | 154.5644
|  |  | 2.25 | 0 | 13.6434 | 16.1241 | 18.6047 | 21.0853 | 23.5659 | 26.0466 | 28.5272 | 31.0078 | 33.4884 | 35.9691 | 38.4497 | 40.9303 | 0 | 0 | 0 | 327.4425
|  |  | 2.75 | 0 | 20.3809 | 24.0866 | 27.7922 | 31.4978 | 35.2034 | 38.9091 | 42.6147 | 46.3203 | 50.0259 | 53.7316 | 57.4372 | 0 | 0 | 0 | 0 | 427.9997
|  |  | 3.25 | 0 | 0 | 33.6416 | 38.8172 | 43.9928 | 49.1684 | 54.3441 | 59.5197 | 64.6953 | 69.8709 | 75.0466 | 80.2222 | 0 | 0 | 0 | 0 | 569.3187
|  |  | 3.75 | 0 | 0 | 44.7891 | 51.6797 | 58.5703 | 65.4609 | 72.3516 | 79.2422 | 86.1328 | 93.0234 | 99.9141 | 106.8047 | 0 | 0 | 0 | 0 | 757.9688
|  |  | 4.25 | 0 | 0 | 0 | 66.3797 | 75.2303 | 84.0809 | 92.9316 | 101.7822 | 110.6328 | 119.4834 | 128.3341 | 137.1847 | 146.0353 | 0 | 0 | 0 | 1062.075
|  |  | 4.75 | 0 | 0 | 0 | 0 | 93.9728 | 105.0284 | 116.0841 | 127.1397 | 138.1953 | 149.2509 | 160.3066 | 171.3622 | 182.4178 | 0 | 0 | 0 | 1243.7578
|  |  | 5.25 | 0 | 0 | 0 | 0 | 0 | 128.3034 | 141.8091 | 155.3147 | 168.8203 | 182.3259 | 195.8316 | 209.3372 | 222.8428 | 0 | 0 | 0 | 1404.585
|  |  | 5.75 | 0 | 0 | 0 | 0 | 0 | 153.9059 | 170.1066 | 186.3072 | 202.5078 | 218.7084 | 234.9091 | 251.1097 | 267.3103 | 0 | 0 | 0 | 1684.865
|  |  | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 200.9766 | 220.1172 | 239.2578 | 258.3984 | 277.5391 | 296.6797 | 0 | 0 | 0 | 0 | 1492.9688
|  |  | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.0703 | 301.3959 | 323.7216 | 346.0472 | 0 | 0 | 0 | 0 | 1250.235
|  |  | 7.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.1897 | 321.9453 | 347.7009 | 373.4566 | 399.2122 | 0 | 0 | 0 | 0 | 1738.5047
|  |  | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.3134 | 426.7441 | 0 | 0 | 0 | 0 | 0 | 824.0575
|  |  | 8.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.5841 | 0 | 0 | 0 | 0 | 0 | 483.5841
|  |  | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543.9766 | 0 | 0 | 0 | 0 | 0 | 543.9766
|  |  | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 3.4453 | 48.0047 | 135.1634 | 222.3375 | 345.9553 | 668.8653 | 940.2487 | 1325.9859 | 1716.9141 | 2244.9656 | 3413.0644 | 2098.1188 | 872.1694 | 39.6594 | 0 | 0
Unconstrained Device Performance
Te
|  |  |  | 4.5 | 5.5 | 6.5 | 7.5 | 8.5 | 9.5 | 10.5 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5
|  | Hs | 0.25 | 0.45137 | 0.74493 | 1.0399 | 1.2837 | 1.3952 | 1.3576 | 1.2232 | 1.0502 | 0.87627 | 0.72011 | 0.58829 | 0.48026 | 0.39326 | 0.32358 | 0.26777 | 0.22294
|  |  | 0.75 | 4.056 | 6.6826 | 9.2955 | 11.3962 | 12.3045 | 11.931 | 10.7427 | 9.2285 | 7.7087 | 6.343 | 5.187 | 4.2409 | 3.477 | 2.8637 | 2.3729 | 1.9785
|  |  | 1.25 | 11.2397 | 18.4873 | 25.6231 | 31.2207 | 33.5107 | 32.3936 | 29.1431 | 25.0486 | 20.9441 | 17.2525 | 14.1235 | 11.5566 | 9.485 | 7.8233 | 6.488 | 5.4155
|  |  | 1.75 | 21.9746 | 36.084 | 49.8398 | 60.3739 | 64.4722 | 62.1496 | 55.8794 | 48.0455 | 40.2092 | 33.155 | 27.1682 | 22.2516 | 18.2752 | 15.0885 | 12.5302 | 10.466
|  |  | 2.25 | 36.2331 | 59.3992 | 81.7656 | 98.5269 | 104.7257 | 100.7049 | 90.4787 | 77.837 | 65.1966 | 53.8077 | 44.1194 | 36.1668 | 29.7384 | 24.5681 | 20.4211 | 17.0727
|  |  | 2.75 | 53.9884 | 88.3613 | 121.2415 | 145.3727 | 153.8779 | 147.641 | 132.5773 | 114.1003 | 95.6251 | 78.9886 | 64.8365 | 53.1778 | 43.7617 | 36.1832 | 30.1014 | 25.1869
|  |  | 3.25 | 75.2144 | 122.8997 | 168.0945 | 200.6342 | 211.5684 | 202.5935 | 181.839 | 156.5343 | 131.3099 | 108.5276 | 89.1531 | 73.1762 | 60.2653 | 49.8673 | 41.5051 | 34.7674
|  |  | 3.75 | 99.8843 | 162.9455 | 222.1964 | 264.0568 | 277.4945 | 265.2348 | 237.9498 | 204.9423 | 172.0096 | 142.2727 | 116.9632 | 96.0717 | 79.1772 | 65.5645 | 54.6106 | 45.7635
|  |  | 4.25 | 127.9719 | 208.431 | 283.3863 | 335.4024 | 351.3716 | 335.2865 | 300.6696 | 259.0603 | 217.5757 | 180.1375 | 148.1648 | 121.7845 | 100.4351 | 83.2263 | 69.3709 | 58.1734
|  |  | 4.75 | 159.4517 | 259.289 | 351.5139 | 414.4552 | 432.9483 | 412.5173 | 369.8274 | 318.7267 | 267.8643 | 221.8836 | 182.672 | 150.2486 | 123.954 | 102.81 | 85.7518 | 71.9587
|  |  | 5.25 | 194.2978 | 315.4554 | 426.4793 | 501.0636 | 521.997 | 496.6781 | 445.1435 | 383.7792 | 322.7482 | 267.5398 | 220.4094 | 181.4074 | 149.7552 | 124.2495 | 103.696 | 87.0691
|  |  | 5.75 | 232.4853 | 376.866 | 508.131 | 594.9573 | 618.3043 | 587.5726 | 526.4737 | 454.0733 | 382.113 | 316.9777 | 261.2503 | 215.2094 | 177.7682 | 147.5815 | 123.2428 | 103.5439
|  |  | 6.25 | 273.9894 | 443.4589 | 596.3245 | 695.9809 | 721.6761 | 684.9986 | 613.588 | 529.4751 | 445.8563 | 370.1184 | 305.2578 | 251.5534 | 207.9606 | 172.7469 | 144.3418 | 121.3403
|  |  | 6.75 | 318.785 | 515.1713 | 691.0098 | 804.0601 | 831.9251 | 788.8308 | 706.4803 | 609.7755 | 513.7851 | 426.8907 | 352.3205 | 290.5214 | 240.2547 | 199.6787 | 166.9351 | 140.4093
|  |  | 7.25 | 366.8478 | 591.9431 | 792.0263 | 918.8913 | 948.9296 | 898.8877 | 804.9473 | 695.0587 | 586.0274 | 487.145 | 402.3086 | 332.0159 | 274.7284 | 228.4562 | 191.0967 | 160.8184
|  |  | 7.75 | 418.1531 | 673.7313 | 899.2063 | 1040.4773 | 1072.4813 | 1015.0145 | 908.8561 | 785.1217 | 662.3948 | 551.0129 | 455.3612 | 375.9449 | 311.2463 | 258.9554 | 216.7178 | 182.4728
|  |  | 8.25 | 472.6779 | 760.4553 | 1012.5955 | 1168.5191 | 1202.4265 | 1137.0666 | 1018.0011 | 879.7483 | 742.6904 | 618.2249 | 511.2394 | 422.4235 | 349.9229 | 291.2883 | 243.9017 | 205.4659
|  |  | 8.75 | 530.3989 | 852.0675 | 1132.0023 | 1303.0621 | 1338.7274 | 1264.9828 | 1132.4972 | 979.136 | 827.1356 | 688.9965 | 570.1475 | 471.2785 | 390.6015 | 325.3117 | 272.5229 | 229.689
|  |  | 9.25 | 591.2927 | 948.5125 | 1257.3251 | 1443.7662 | 1481.1192 | 1398.5649 | 1252.0977 | 1083.0351 | 915.351 | 763.0011 | 631.8006 | 522.6573 | 433.4217 | 361.1591 | 302.6265 | 255.1824
|  |  | 9.75 | 655.3364 | 1049.7352 | 1388.4647 | 1590.7698 | 1629.6155 | 1537.7823 | 1376.667 | 1191.2876 | 1007.6466 | 840.5173 | 696.4534 | 576.375 | 478.2216 | 398.6844 | 334.3104 | 282.0357
Constrained Device Performance
Te
|  |  |  | 4.5 | 5.5 | 6.5 | 7.5 | 8.5 | 9.5 | 10.5 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5
|  | Hs | 0.25 | 0.36109 | 0.59595 | 0.83194 | 1.027 | 1.1161 | 1.0861 | 0.97857 | 0.84016 | 0.70102 | 0.57609 | 0.47064 | 0.3842 | 0.31461 | 0.25886 | 0.21421 | 0.17835
|  |  | 0.75 | 3.2448 | 5.3461 | 7.4364 | 9.117 | 9.8436 | 9.5448 | 8.5941 | 7.3828 | 6.167 | 5.0744 | 4.1496 | 3.3928 | 2.7816 | 2.2909 | 1.8983 | 1.5828
|  |  | 1.25 | 8.9917 | 14.7898 | 20.4985 | 24.9766 | 26.8086 | 25.9149 | 23.3145 | 20.0389 | 16.7553 | 13.802 | 11.2988 | 9.2453 | 7.588 | 6.2587 | 5.1904 | 4.3324
|  |  | 1.75 | 17.5797 | 28.8672 | 39.8719 | 48.2991 | 51.5777 | 49.7197 | 44.7035 | 38.4364 | 32.1674 | 26.524 | 21.7346 | 17.8013 | 14.6202 | 12.0708 | 10.0241 | 8.3728
|  |  | 2.25 | 28.9865 | 47.5194 | 65.4124 | 78.8215 | 83.7806 | 80.5639 | 72.383 | 62.2696 | 52.1572 | 43.0462 | 35.2955 | 28.9335 | 23.7907 | 19.6545 | 16.3369 | 13.6582
|  |  | 2.75 | 43.1907 | 70.689 | 96.9932 | 116.2981 | 123.1023 | 118.1128 | 106.0618 | 91.2803 | 76.5001 | 63.1909 | 51.8692 | 42.5422 | 35.0093 | 28.9466 | 24.0811 | 20.1495
|  |  | 3.25 | 60.1715 | 98.3198 | 134.4756 | 160.5074 | 169.2547 | 162.0748 | 145.4712 | 125.2275 | 105.0479 | 86.8221 | 71.3225 | 58.5409 | 48.2122 | 39.8938 | 33.2041 | 27.8139
|  |  | 3.75 | 79.9074 | 130.3564 | 177.7571 | 211.2454 | 221.9956 | 212.1879 | 190.3599 | 163.9539 | 137.6077 | 113.8182 | 93.5706 | 76.8574 | 63.3417 | 52.4516 | 43.6885 | 36.6108
|  |  | 4.25 | 102.3775 | 166.7448 | 226.7091 | 268.3219 | 281.0973 | 268.2292 | 240.5356 | 207.2482 | 174.0606 | 144.11 | 118.5318 | 97.4276 | 80.3481 | 66.581 | 55.4967 | 46.5387
|  |  | 4.75 | 127.5613 | 207.4312 | 281.2111 | 286 | 286 | 286 | 286 | 254.9814 | 214.2914 | 177.5069 | 146.1376 | 120.1988 | 99.1632 | 82.248 | 68.6014 | 57.5669
|  |  | 5.25 | 155.4382 | 252.3643 | 286 | 286 | 286 | 286 | 286 | 286 | 258.1986 | 214.0318 | 176.3275 | 145.1259 | 119.8042 | 99.3996 | 82.9568 | 69.6553
|  |  | 5.75 | 185.9882 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 253.5822 | 209.0003 | 172.1675 | 142.2146 | 118.0652 | 98.5942 | 82.8351
|  |  | 6.25 | 219.1915 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 244.2063 | 201.2427 | 166.3685 | 138.1975 | 115.4735 | 97.0722
|  |  | 6.75 | 255.028 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 281.8564 | 232.4171 | 192.2037 | 159.7429 | 133.5481 | 112.3274
|  |  | 7.25 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 265.6127 | 219.7827 | 182.765 | 152.8773 | 128.6547
|  |  | 7.75 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 248.997 | 207.1643 | 173.3742 | 145.9782
|  |  | 8.25 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 279.9384 | 233.0307 | 195.1214 | 164.3727
|  |  | 8.75 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 260.2494 | 218.0184 | 183.7512
|  |  | 9.25 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 242.1012 | 204.1459
|  |  | 9.75 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 267.4483 | 225.6286
Economic Parameters (Utility Generator Model)
| Plant Life (years) |  |  |  |  | 20
| Federal Tax Rate |  |  |  |  | 40%
| State Tax Rate |  |  |  |  | 0%
| Effective Tax Rate |  |  |  |  | 40%
| Construction Finance Rate |  |  |  |  | 8%
| % Construction Spending during Year 0 |  |  |  |  | 50%
| % Construction Spending during Year 1 |  |  |  |  | 50%
| Equity |  |  |  |  | 50%
| Return on Equity |  |  |  |  | 9.7%
| Debt |  |  |  |  | 50%
| Return on Debt |  |  |  |  | 8%
| Weighted Average Cost of Capital (After tax) |  |  |  |  | 7.25%
| MACRS Depreciation |  |  |  | Year 1 | 20%
[5 empty] | Year 2 | 32%
[5 empty] | Year 3 | 19.2%
[5 empty] | Year 4 | 11.52%
[5 empty] | Year 5 | 11.52%
[5 empty] | Year 6 | 5.76%
| Annual Construction Multiplier - Year 1 |  |  |  |  | 1.0235 | 1+(1-T)*[ (1+ (Construction Finance Rate))^(t+0.5) - 1 ]
| Annual Construction Multiplier - Year 2 |  |  |  |  | 1.0734 | 1+(1-T)*[ (1+ (Construction Finance Rate))^(t+0.5) - 1 ]
| Construction Cost Multiplier (CCMult) |  |  |  |  | 1.0485
| Capital Recovery Factor (WACC,Plant Life) |  |  |  |  | 0.096235
| PVdepr |  |  |  |  | 0.82641
| Fixed Charge Rate |  |  |  |  | 11.26% | CCmult*CRF*(1-T*PVdepr)/(1-T)

## CBS (CoE)
Plant Rated Capacity (kW) | [5 empty] | 286 |  | 2860 |  | 14300 |  | 28600
MWh/Year | [5 empty] | 700.7352 |  | 7007.3523 |  | 35036.7617 |  | 70073.5235
Cost Breakdown Structure for WEC Rated at 286 kW | [5 empty] | Units
[5 empty] | Weight (tonnes) | 1 | in% | 10 | in% | 50 | in % | 100 | in %
1 | Capex
1.1 |  | Development |  |  |  | 73.1526 | 26.04% | 14.0956 | 14.34% | 3.5354 | 5.313% | 1.7383 | 2.776%
1.1.1 |  |  | Permitting and Environmental Compliance |  |  | 57.8761 | 20.6% | 11.021 | 11.21% | 2.2548 | 3.388% | 1.1274 | 1.8%
1.1.1.1 |  |  |  | Siting & Scoping |  | 5.382 | 1.916% | 0.68279 | 0.6948% | 0.13656 | 0.2052% | 0.068279 | 0.109%
1.1.1.2 |  |  |  | Pre-Installation Studies |  | 26.227 | 9.337% | 4.5787 | 4.659% | 0.89405 | 1.344% | 0.44702 | 0.7138%
1.1.1.3 |  |  |  | Post-Installation Studies |  | 11.4065 | 4.061% | 3.6469 | 3.711% | 0.72938 | 1.096% | 0.36469 | 0.5824%
1.1.1.4 |  |  |  | NEPA & Process |  | 14.8606 | 5.29% | 2.1126 | 2.15% | 0.49482 | 0.7436% | 0.24741 | 0.3951%
1.1.2 |  |  | Site Assessment |  |  | 3.1161 | 1.109% | 0.47242 | 0.4807% | 0.094485 | 0.142% | 0.047242 | 0.07544%
1.1.3 |  |  | Project Design, Engineering, and Management |  |  | 12.1604 | 4.329% | 2.6022 | 2.648% | 1.1861 | 1.783% | 0.56366 | 0.9001%
1.2 |  | Infrastructure |  |  |  | 15.9049 | 5.662% | 7.8078 | 7.945% | 2.431 | 3.653% | 2.7809 | 4.441%
1.2.1 |  |  | Subsea Cables |  |  | 14.459 | 5.147% | 1.4459 | 1.471% | 1.0796 | 1.622% | 1.3977 | 2.232%
1.2.2 |  |  | Terminations and Connectors |  |  | 1.4459 | 0.5147% | 0.14459 | 0.1471% | 0.10796 | 0.1622% | 0.13977 | 0.2232%
1.2.3 |  |  | Dockside Improvements |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.2.4 |  |  | Dedicated O&M Vessel |  |  | 0 | 0% | 6.2174 | 6.326% | 1.2435 | 1.869% | 1.2435 | 1.986%
1.2.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.3 |  | Mooring/Foundation |  |  |  | 8.4308 | 3.001% | 7.5877 | 7.721% | 7.5877 | 11.4% | 7.5877 | 12.12%
1.3.1 |  |  | Mooring lines/chain |  |  | 2.9316 | 1.044% | 2.6384 | 2.685% | 2.6384 | 3.965% | 2.6384 | 4.213%
1.3.2 |  |  | Anchors |  |  | 2.8918 | 1.029% | 2.6026 | 2.648% | 2.6026 | 3.911% | 2.6026 | 4.156%
1.3.3 |  |  | Buoyancy |  |  | 0.96393 | 0.3432% | 0.86754 | 0.8827% | 0.86754 | 1.304% | 0.86754 | 1.385%
1.3.4 |  |  | Connecting Hardware (shackles etc.) |  |  | 1.6435 | 0.5851% | 1.4792 | 1.505% | 1.4792 | 2.223% | 1.4792 | 2.362%
1.3.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.4 |  | Device Structural Components |  |  | 687.2862 | 47.2174 | 16.81% | 33.215 | 33.8% | 29.4155 | 44.21% | 28.5859 | 45.65%
1.4.1 |  |  | Surface Float |  | 205.44 | 14.3665 | 5.114% | 9.994 | 10.17% | 8.7956 | 13.22% | 8.5226 | 13.61%
1.4.2 |  |  | Vertical Column |  | 223.64 | 14.8021 | 5.269% | 10.5148 | 10.7% | 9.368 | 14.08% | 9.1297 | 14.58%
1.4.3 |  |  | Reaction Plate |  | 244.73 | 17.1231 | 6.096% | 12.0549 | 12.27% | 10.6751 | 16.04% | 10.3732 | 16.56%
1.4.4 |  |  | Device Access (Railings, Ladders, etc) |  | 13.4762 | 0.92583 | 0.3296% | 0.65127 | 0.6627% | 0.57677 | 0.8668% | 0.56051 | 0.8951%
1.5 |  | Power Take Off |  |  | 12.4628 | 10.0163 | 3.566% | 7.9313 | 8.07% | 6.9675 | 10.47% | 6.6325 | 10.59%
1.5.1 |  |  | Generator |  | 2.0735 | 0.41353 | 0.1472% | 0.36485 | 0.3712% | 0.33427 | 0.5023% | 0.32191 | 0.514%
1.5.2 |  |  | Hydraulic Components (all) |  | 7.9555 | 1.8498 | 0.6585% | 1.6869 | 1.716% | 1.5817 | 2.377% | 1.5384 | 2.457%
1.5.3 |  |  | Hydraulic Energy Storage |  | 1.2927 | 0.90976 | 0.3239% | 0.58546 | 0.5957% | 0.43023 | 0.6465% | 0.37677 | 0.6017%
1.5.4 |  |  | Frequency Converter |  | 1.1411 | 1.3784 | 0.4907% | 0.65384 | 0.6653% | 0.38821 | 0.5834% | 0.31015 | 0.4953%
1.5.5 |  |  | Step-up Transformer |  | 0 | 0.91895 | 0.3271% | 0.79583 | 0.8098% | 0.71971 | 1.082% | 0.68921 | 1.101%
1.5.6 |  |  | Riser Cable |  | 0 | 1.4138 | 0.5033% | 1.4138 | 1.439% | 1.4138 | 2.125% | 1.4138 | 2.258%
1.5.7 |  |  | Electrical Energy Storage |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.8 |  |  | Seals |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.9 |  |  | Control System |  | 0 | 0.090666 | 0.03228% | 0.08534 | 0.08684% | 0.081805 | 0.1229% | 0.080328 | 0.1283%
1.5.10 |  |  | Bearings and Linear Guides |  | 0 | 1.4204 | 0.5056% | 1.2301 | 1.252% | 1.1124 | 1.672% | 1.0653 | 1.701%
1.5.11 |  |  | Assembly, Testing & QA |  | 0 | 0.93181 | 0.3317% | 0.80698 | 0.8211% | 0.72979 | 1.097% | 0.69887 | 1.116%
1.5.12 |  |  | PTO mounting |  | 0 | 0.45947 | 0.1636% | 0.20548 | 0.2091% | 0.11708 | 0.176% | 0.091895 | 0.1467%
1.5.13 |  |  | Other |  | 0 | 0.22974 | 0.08178% | 0.10274 | 0.1045% | 0.058542 | 0.08798% | 0.045947 | 0.07337%
1.6 |  | Subsystem Integration & Profit Margin |  |  |  | 5.7234 | 2.037% | 4.1146 | 4.187% | 3.6383 | 5.468% | 3.5218 | 5.624%
1.7 |  | Installation |  |  |  | 94.9235 | 33.79% | 14.5907 | 14.85% | 6.9182 | 10.4% | 6.0823 | 9.713%
1.7.1 |  |  | Transport to Staging Site |  |  | 0.47795 | 0.1701% | 0.47795 | 0.4863% | 0.47795 | 0.7183% | 0.47795 | 0.7632%
1.7.2 |  |  | Cable Shore Landing |  |  | 10.7157 | 3.815% | 1.2325 | 1.254% | 0.24651 | 0.3705% | 0.24645 | 0.3935%
1.7.3 |  |  | Mooring/Foundation System |  |  | 51.3106 | 18.27% | 6.2729 | 6.383% | 2.2697 | 3.411% | 1.7693 | 2.825%
1.7.4 |  |  | Cable Installation |  |  | 24.2193 | 8.622% | 3.6632 | 3.727% | 1.4471 | 2.175% | 1.1701 | 1.869%
1.7.5 |  |  | Device Installation |  |  | 4.1 | 1.46% | 1.472 | 1.498% | 1.2385 | 1.861% | 1.2093 | 1.931%
1.7.6 |  |  | Device Comissioning |  |  | 4.1 | 1.46% | 1.472 | 1.498% | 1.2385 | 1.861% | 1.2093 | 1.931%
1.8 |  | Decommissioning |  |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.9 |  | Contingency |  |  |  | 25.5369 | 9.091% | 8.9343 | 9.091% | 6.0494 | 9.091% | 5.693 | 9.091%
Total Installed Cost (omits Decommissioning) |  |  |  |  | 699.749 | 280.9058 | 100% | 98.277 | 100% | 66.543 | 100% | 62.6225 | 100%
2 | Annualized OPEX |  |  |  |  | 166.5079 | 59.28% | 47.0177 | 47.84% | 18.883 | 28.38% | 13.3557 | 21.33%
2.1 |  | Insurance |  |  |  | 32.3719 | 11.52% | 13.3681 | 13.6% | 5.0595 | 7.603% | 2.4513 | 3.914%
2.2 |  | Environmental Monitoring and Regulatory Compliance |  |  |  | 101.3221 | 36.07% | 15.9975 | 16.28% | 3.1995 | 4.808% | 1.5997 | 2.555%
2.3 |  | Marine Operations |  |  |  | 3.7916 | 1.35% | 3.7916 | 3.858% | 1.6049 | 2.412% | 1.6049 | 2.563%
2.4 |  | Shoreside Operations |  |  |  | 20.2018 | 7.192% | 5.7074 | 5.807% | 1.2978 | 1.95% | 0.96275 | 1.537%
2.5 |  | Replacement Parts |  |  |  | 7.6788 | 2.734% | 7.0114 | 7.134% | 6.5797 | 9.888% | 5.5954 | 8.935%
2.6 |  | Consumables |  |  |  | 1.1417 | 0.4064% | 1.1417 | 1.162% | 1.1417 | 1.716% | 1.1417 | 1.823%
Total Annual OPEX | [5 empty] | 166.5079 | 59.28% | 47.0177 | 47.84% | 18.883 | 28.38% | 13.3557 | 21.33%

## CBS ($ per kW)
Plant Rated Capacity (kW) | [5 empty] | 286 |  | 2860 |  | 14300 |  | 28600
Cost Breakdown Structure for WEC Rated at 286 kW | [5 empty] | Units
[5 empty] | Weight (tonnes) | 1 | in% | 10 | in% | 50 | in % | 100 | in %
1 | Capex
1.1 |  | Development |  |  |  | 15920.9419 | 26.04% | 3067.7663 | 14.34% | 769.4517 | 5.313% | 378.3238 | 2.776%
1.1.1 |  |  | Permitting and Environmental Compliance |  |  | 12596.1538 | 20.6% | 2398.6014 | 11.21% | 490.7343 | 3.388% | 245.3671 | 1.8%
1.1.1.1 |  |  |  | Siting & Scoping |  | 1171.3287 | 1.916% | 148.6014 | 0.6948% | 29.7203 | 0.2052% | 14.8601 | 0.109%
1.1.1.2 |  |  |  | Pre-Installation Studies |  | 5708.042 | 9.337% | 996.5035 | 4.659% | 194.5804 | 1.344% | 97.2902 | 0.7138%
1.1.1.3 |  |  |  | Post-Installation Studies |  | 2482.5175 | 4.061% | 793.7063 | 3.711% | 158.7413 | 1.096% | 79.3706 | 0.5824%
1.1.1.4 |  |  |  | NEPA & Process |  | 3234.2657 | 5.29% | 459.7902 | 2.15% | 107.6923 | 0.7436% | 53.8462 | 0.3951%
1.1.2 |  |  | Site Assessment |  |  | 678.1923 | 1.109% | 102.8185 | 0.4807% | 20.5637 | 0.142% | 10.2819 | 0.07544%
1.1.3 |  |  | Project Design, Engineering, and Management |  |  | 2646.5958 | 4.329% | 566.3463 | 2.648% | 258.1537 | 1.783% | 122.6748 | 0.9001%
1.2 |  | Infrastructure |  |  |  | 3461.5385 | 5.662% | 1699.3007 | 7.945% | 529.0909 | 3.653% | 605.2448 | 4.441%
1.2.1 |  |  | Subsea Cables |  |  | 3146.8531 | 5.147% | 314.6853 | 1.471% | 234.965 | 1.622% | 304.1958 | 2.232%
1.2.2 |  |  | Terminations and Connectors |  |  | 314.6853 | 0.5147% | 31.4685 | 0.1471% | 23.4965 | 0.1622% | 30.4196 | 0.2232%
1.2.3 |  |  | Dockside Improvements |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.2.4 |  |  | Dedicated O&M Vessel |  |  | 0 | 0% | 1353.1469 | 6.326% | 270.6294 | 1.869% | 270.6294 | 1.986%
1.2.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.3 |  | Mooring/Foundation |  |  |  | 1834.8776 | 3.001% | 1651.3899 | 7.721% | 1651.3899 | 11.4% | 1651.3899 | 12.12%
1.3.1 |  |  | Mooring lines/chain |  |  | 638.0245 | 1.044% | 574.222 | 2.685% | 574.222 | 3.965% | 574.222 | 4.213%
1.3.2 |  |  | Anchors |  |  | 629.3706 | 1.029% | 566.4336 | 2.648% | 566.4336 | 3.911% | 566.4336 | 4.156%
1.3.3 |  |  | Buoyancy |  |  | 209.7902 | 0.3432% | 188.8112 | 0.8827% | 188.8112 | 1.304% | 188.8112 | 1.385%
1.3.4 |  |  | Connecting Hardware (shackles etc.) |  |  | 357.6923 | 0.5851% | 321.9231 | 1.505% | 321.9231 | 2.223% | 321.9231 | 2.362%
1.3.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.4 |  | Device Structural Components |  |  | 687.2862 | 10276.4069 | 16.81% | 7228.9127 | 33.8% | 6401.9845 | 44.21% | 6221.4452 | 45.65%
1.4.1 |  |  | Surface Float |  | 205.44 | 3126.7173 | 5.114% | 2175.1002 | 10.17% | 1914.2716 | 13.22% | 1854.8497 | 13.61%
1.4.2 |  |  | Vertical Column |  | 223.64 | 3221.5289 | 5.269% | 2288.439 | 10.7% | 2038.8511 | 14.08% | 1986.9874 | 14.58%
1.4.3 |  |  | Reaction Plate |  | 244.73 | 3726.6625 | 6.096% | 2623.6301 | 12.27% | 2323.3328 | 16.04% | 2257.619 | 16.56%
1.4.4 |  |  | Device Access (Railings, Ladders, etc) |  | 13.4762 | 201.4982 | 0.3296% | 141.7434 | 0.6627% | 125.5291 | 0.8668% | 121.9891 | 0.8951%
1.5 |  | Power Take Off |  |  | 12.4628 | 2179.9428 | 3.566% | 1726.1656 | 8.07% | 1516.4034 | 10.47% | 1443.493 | 10.59%
1.5.1 |  |  | Generator |  | 2.0735 | 90 | 0.1472% | 79.4062 | 0.3712% | 72.751 | 0.5023% | 70.0594 | 0.514%
1.5.2 |  |  | Hydraulic Components (all) |  | 7.9555 | 402.59 | 0.6585% | 367.1398 | 1.716% | 344.2315 | 2.377% | 334.8112 | 2.457%
1.5.3 |  |  | Hydraulic Energy Storage |  | 1.2927 | 198 | 0.3239% | 127.4206 | 0.5957% | 93.6351 | 0.6465% | 82 | 0.6017%
1.5.4 |  |  | Frequency Converter |  | 1.1411 | 300 | 0.4907% | 142.3025 | 0.6653% | 84.4909 | 0.5834% | 67.5 | 0.4953%
1.5.5 |  |  | Step-up Transformer |  | 0 | 200 | 0.3271% | 173.2051 | 0.8098% | 156.6377 | 1.082% | 150 | 1.101%
1.5.6 |  |  | Riser Cable |  | 0 | 307.6923 | 0.5033% | 307.6923 | 1.439% | 307.6923 | 2.125% | 307.6923 | 2.258%
1.5.7 |  |  | Electrical Energy Storage |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.8 |  |  | Seals |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.9 |  |  | Control System |  | 0 | 19.7325 | 0.03228% | 18.5735 | 0.08684% | 17.804 | 0.1229% | 17.4825 | 0.1283%
1.5.10 |  |  | Bearings and Linear Guides |  | 0 | 309.128 | 0.5056% | 267.7128 | 1.252% | 242.1057 | 1.672% | 231.8462 | 1.701%
1.5.11 |  |  | Assembly, Testing & QA |  | 0 | 202.8 | 0.3317% | 175.6308 | 0.8211% | 158.8319 | 1.097% | 152.1014 | 1.116%
1.5.12 |  |  | PTO mounting |  | 0 | 100 | 0.1636% | 44.7214 | 0.2091% | 25.4821 | 0.176% | 20 | 0.1467%
1.5.13 |  |  | Other |  | 0 | 50 | 0.08178% | 22.3607 | 0.1045% | 12.7411 | 0.08798% | 10 | 0.07337%
1.6 |  | Subsystem Integration & Profit Margin |  |  |  | 1245.635 | 2.037% | 895.5078 | 4.187% | 791.8388 | 5.468% | 766.4938 | 5.624%
1.7 |  | Installation |  |  |  | 20659.169 | 33.79% | 3175.5151 | 14.85% | 1505.6801 | 10.4% | 1323.7619 | 9.713%
1.7.1 |  |  | Transport to Staging Site |  |  | 104.021 | 0.1701% | 104.021 | 0.4863% | 104.021 | 0.7183% | 104.021 | 0.7632%
1.7.2 |  |  | Cable Shore Landing |  |  | 2332.1678 | 3.815% | 268.2517 | 1.254% | 53.6503 | 0.3705% | 53.6364 | 0.3935%
1.7.3 |  |  | Mooring/Foundation System |  |  | 11167.2502 | 18.27% | 1365.2303 | 6.383% | 493.9833 | 3.411% | 385.0774 | 2.825%
1.7.4 |  |  | Cable Installation |  |  | 5271.0971 | 8.622% | 797.2603 | 3.727% | 314.9521 | 2.175% | 254.6635 | 1.869%
1.7.5 |  |  | Device Installation |  |  | 892.3164 | 1.46% | 320.3759 | 1.498% | 269.5367 | 1.861% | 263.1818 | 1.931%
1.7.6 |  |  | Device Comissioning |  |  | 892.3164 | 1.46% | 320.3759 | 1.498% | 269.5367 | 1.861% | 263.1818 | 1.931%
1.8 |  | Decommissioning |  |  |  | 20659.169 | 33.79% | 3175.5151 | 14.85% | 1505.6801 | 10.4% | 1323.7619 | 9.713%
1.9 |  | Contingency |  |  |  | 5557.8512 | 9.091% | 1944.4558 | 9.091% | 1316.5839 | 9.091% | 1239.0152 | 9.091%
Total Installed Cost (omits Decommissioning) |  |  |  |  | 699.749 | 61136.3629 | 100% | 21389.0137 | 100% | 14482.4232 | 100% | 13629.1676 | 100%
2 | Annualized OPEX |  |  |  |  | 4079.6482 | 6.673% | 1151.9904 | 5.386% | 462.6572 | 3.195% | 327.2322 | 2.401%
2.1 |  | Insurance |  |  |  | 793.1514 | 1.297% | 327.5358 | 1.531% | 123.9639 | 0.856% | 60.0591 | 0.4407%
2.2 |  | Environmental Monitoring and Regulatory Compliance |  |  |  | 2482.5175 | 4.061% | 391.958 | 1.833% | 78.3916 | 0.5413% | 39.1958 | 0.2876%
2.3 |  | Marine Operations |  |  |  | 92.8986 | 0.152% | 92.8986 | 0.4343% | 39.3231 | 0.2715% | 39.3231 | 0.2885%
2.4 |  | Shoreside Operations |  |  |  | 494.9685 | 0.8096% | 139.8378 | 0.6538% | 31.7966 | 0.2196% | 23.5886 | 0.1731%
2.5 |  | Replacement Parts |  |  |  | 188.1401 | 0.3077% | 171.7881 | 0.8032% | 161.21 | 1.113% | 137.0935 | 1.006%
2.6 |  | Consumables |  |  |  | 27.972 | 0.04575% | 27.972 | 0.1308% | 27.972 | 0.1931% | 27.972 | 0.2052%
Total Annual OPEX | [5 empty] | 4079.6482 | 6.673% | 1151.9904 | 5.386% | 462.6572 | 3.195% | 327.2322 | 2.401%

## CBS (Total)
Cost Breakdown Structure for WEC Rated at 286 kW | [5 empty] | Units
[5 empty] | Weight (tonnes) | 1 | in% | 10 | in% | 50 | in % | 100 | in %
1 | Capex
1.1 |  | Development |  |  |  | 4553389.3975 | 26.04% | 8773811.5558 | 14.34% | 11003159.0788 | 5.313% | 10820059.5912 | 2.776%
1.1.1 |  |  | Permitting and Environmental Compliance |  |  | 3602500 | 20.6% | 6860000 | 11.21% | 7017500 | 3.388% | 7017500 | 1.8%
1.1.1.1 |  |  |  | Siting & Scoping |  | 335000 | 1.916% | 425000 | 0.6948% | 425000 | 0.2052% | 425000 | 0.109%
1.1.1.2 |  |  |  | Pre-Installation Studies |  | 1632500 | 9.337% | 2850000 | 4.659% | 2782500 | 1.344% | 2782500 | 0.7138%
1.1.1.3 |  |  |  | Post-Installation Studies |  | 710000 | 4.061% | 2270000 | 3.711% | 2270000 | 1.096% | 2270000 | 0.5824%
1.1.1.4 |  |  |  | NEPA & Process |  | 925000 | 5.29% | 1315000 | 2.15% | 1540000 | 0.7436% | 1540000 | 0.3951%
1.1.2 |  |  | Site Assessment |  |  | 193963 | 1.109% | 294061 | 0.4807% | 294061 | 0.142% | 294061 | 0.07544%
1.1.3 |  |  | Project Design, Engineering, and Management |  |  | 756926.3975 | 4.329% | 1619750.5558 | 2.648% | 3691598.0788 | 1.783% | 3508498.5912 | 0.9001%
1.2 |  | Infrastructure |  |  |  | 990000 | 5.662% | 4860000 | 7.945% | 7566000 | 3.653% | 17310000 | 4.441%
1.2.1 |  |  | Subsea Cables |  |  | 900000 | 5.147% | 900000 | 1.471% | 3360000 | 1.622% | 8700000 | 2.232%
1.2.2 |  |  | Terminations and Connectors |  |  | 90000 | 0.5147% | 90000 | 0.1471% | 336000 | 0.1622% | 870000 | 0.2232%
1.2.3 |  |  | Dockside Improvements |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.2.4 |  |  | Dedicated O&M Vessel |  |  | 0 | 0% | 3870000 | 6.326% | 3870000 | 1.869% | 7740000 | 1.986%
1.2.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.3 |  | Mooring/Foundation |  |  |  | 524775 | 3.001% | 4722975 | 7.721% | 23614875 | 11.4% | 47229750 | 12.12%
1.3.1 |  |  | Mooring lines/chain |  |  | 182475 | 1.044% | 1642275 | 2.685% | 8211375 | 3.965% | 16422750 | 4.213%
1.3.2 |  |  | Anchors |  |  | 180000 | 1.029% | 1620000 | 2.648% | 8100000 | 3.911% | 16200000 | 4.156%
1.3.3 |  |  | Buoyancy |  |  | 60000 | 0.3432% | 540000 | 0.8827% | 2700000 | 1.304% | 5400000 | 1.385%
1.3.4 |  |  | Connecting Hardware (shackles etc.) |  |  | 102300 | 0.5851% | 920700 | 1.505% | 4603500 | 2.223% | 9207000 | 2.362%
1.3.5 |  |  | Other |  |  | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.4 |  | Device Structural Components |  |  | 687.2862 | 2939052.3699 | 16.81% | 20674690.1967 | 33.8% | 91548379.0369 | 44.21% | 177933334.054 | 45.65%
1.4.1 |  |  | Surface Float |  | 205.44 | 894241.1454 | 5.114% | 6220786.6201 | 10.17% | 27374083.7994 | 13.22% | 53048701.149 | 13.61%
1.4.2 |  |  | Vertical Column |  | 223.64 | 921357.2792 | 5.269% | 6544935.441 | 10.7% | 29155570.0724 | 14.08% | 56827841.0474 | 14.58%
1.4.3 |  |  | Reaction Plate |  | 244.73 | 1065825.4675 | 6.096% | 7503582.0534 | 12.27% | 33223658.9095 | 16.04% | 64567902.9546 | 16.56%
1.4.4 |  |  | Device Access (Railings, Ladders, etc) |  | 13.4762 | 57628.4778 | 0.3296% | 405386.0823 | 0.6627% | 1795066.2556 | 0.8668% | 3488888.903 | 0.8951%
1.5 |  | Power Take Off |  |  | 12.4628 | 623463.648 | 3.566% | 4936833.4731 | 8.07% | 21684568.7466 | 10.47% | 41283900 | 10.59%
1.5.1 |  |  | Generator |  | 2.0735 | 25740 | 0.1472% | 227101.823 | 0.3712% | 1040339.5245 | 0.5023% | 2003700 | 0.514%
1.5.2 |  |  | Hydraulic Components (all) |  | 7.9555 | 115140.74 | 0.6585% | 1050019.8426 | 1.716% | 4922510.8914 | 2.377% | 9575600 | 2.457%
1.5.3 |  |  | Hydraulic Energy Storage |  | 1.2927 | 56628 | 0.3239% | 364422.8116 | 0.5957% | 1338982.0596 | 0.6465% | 2345200 | 0.6017%
1.5.4 |  |  | Frequency Converter |  | 1.1411 | 85800 | 0.4907% | 406985.1349 | 0.6653% | 1208220.1022 | 0.5834% | 1930500 | 0.4953%
1.5.5 |  |  | Step-up Transformer |  | 0 | 57200 | 0.3271% | 495366.531 | 0.8098% | 2239919.7042 | 1.082% | 4290000 | 1.101%
1.5.6 |  |  | Riser Cable |  | 0 | 88000 | 0.5033% | 880000 | 1.439% | 4400000 | 2.125% | 8800000 | 2.258%
1.5.7 |  |  | Electrical Energy Storage |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.8 |  |  | Seals |  | 0 | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0%
1.5.9 |  |  | Control System |  | 0 | 5643.5 | 0.03228% | 53120.1468 | 0.08684% | 254597.342 | 0.1229% | 500000 | 0.1283%
1.5.10 |  |  | Bearings and Linear Guides |  | 0 | 88410.608 | 0.5056% | 765658.579 | 1.252% | 3462111.4432 | 1.672% | 6630800 | 1.701%
1.5.11 |  |  | Assembly, Testing & QA |  | 0 | 58000.8 | 0.3317% | 502303.9718 | 0.8211% | 2271296.3216 | 1.097% | 4350100 | 1.116%
1.5.12 |  |  | PTO mounting |  | 0 | 28600 | 0.1636% | 127903.0883 | 0.2091% | 364394.2387 | 0.176% | 572000 | 0.1467%
1.5.13 |  |  | Other |  | 0 | 14300 | 0.08178% | 63951.5442 | 0.1045% | 182197.1193 | 0.08798% | 286000 | 0.07337%
1.6 |  | Subsystem Integration & Profit Margin |  |  |  | 356251.6018 | 2.037% | 2561152.367 | 4.187% | 11323294.7784 | 5.468% | 21921723.4054 | 5.624%
1.7 |  | Installation |  |  |  | 5908522.33 | 33.79% | 9081973.1556 | 14.85% | 21531225.3778 | 10.4% | 37859590.6556 | 9.713%
1.7.1 |  |  | Transport to Staging Site |  |  | 29750 | 0.1701% | 297500 | 0.4863% | 1487500 | 0.7183% | 2975000 | 0.7632%
1.7.2 |  |  | Cable Shore Landing |  |  | 667000 | 3.815% | 767200 | 1.254% | 767200 | 0.3705% | 1534000 | 0.3935%
1.7.3 |  |  | Mooring/Foundation System |  |  | 3193833.55 | 18.27% | 3904558.5556 | 6.383% | 7063960.7778 | 3.411% | 11013213.5556 | 2.825%
1.7.4 |  |  | Cable Installation |  |  | 1507533.78 | 8.622% | 2280164.6 | 3.727% | 4503814.6 | 2.175% | 7283377.1 | 1.869%
1.7.5 |  |  | Device Installation |  |  | 255202.5 | 1.46% | 916275 | 1.498% | 3854375 | 1.861% | 7527000 | 1.931%
1.7.6 |  |  | Device Comissioning |  |  | 255202.5 | 1.46% | 916275 | 1.498% | 3854375 | 1.861% | 7527000 | 1.931%
1.8 |  | Decommissioning |  |  |  | 5908522.33 | 8.547% | 9081973.1556 | 8.778% | 21531225.3778 | 8.898% | 37859590.6556 | 8.993%
1.9 |  | Contingency |  |  |  | 1589545.4347 | 9.091% | 5561143.5748 | 9.091% | 18827150.2018 | 9.091% | 35435835.7706 | 9.091%
Total Installed Cost (omits Decommissioning) |  |  |  |  | 699.749 | 17484999.782 | 99.46% | 61172579.3229 | 99.69% | 207098652.2203 | 99.81% | 389794193.4768 | 99.9%
2 | Annualized OPEX |  |  |  |  | 1166779.3723 | 6.673% | 3294692.4979 | 5.386% | 6615998.4863 | 3.195% | 9358840.3906 | 2.401%
2.1 |  | Insurance |  |  |  | 226841.299 | 1.297% | 936752.4838 | 1.531% | 1772683.4294 | 0.856% | 1717691.4906 | 0.4407%
2.2 |  | Environmental Monitoring and Regulatory Compliance |  |  |  | 710000 | 4.061% | 1121000 | 1.833% | 1121000 | 0.5413% | 1121000 | 0.2876%
2.3 |  | Marine Operations |  |  |  | 26569 | 0.152% | 265690 | 0.4343% | 562320 | 0.2715% | 1124640 | 0.2885%
2.4 |  | Shoreside Operations |  |  |  | 141561 | 0.8096% | 399936 | 0.6538% | 454692 | 0.2196% | 674634 | 0.1731%
2.5 |  | Replacement Parts |  |  |  | 53808.0733 | 0.3077% | 491314.0141 | 0.8032% | 2305303.0569 | 1.113% | 3920874.9 | 1.006%
2.6 |  | Consumables |  |  |  | 8000 | 0.04575% | 80000 | 0.1308% | 400000 | 0.1931% | 800000 | 0.2052%
Total Annual OPEX | [5 empty] | 1166779.3723 | 6.673% | 3294692.4979 | 5.386% | 6615998.4863 | 3.195% | 9358840.3906 | 2.401%

## 1.1
1.1 Development
Cost Summary
|  |  | 1-Unit | 10-Units | 50-Units | 100-Units
| 1.1.1.1 | Siting & Scoping | 335000 | 425000 | 425000 | 425000
| 1.1.1.2 | Pre-Installation Studies | 1632500 | 2850000 | 2782500 | 2782500
| 1.1.1.3 | Post-Installation Studies | 710000 | 2270000 | 2270000 | 2270000
| 1.1.1.4 | NEPA & Process | 925000 | 1315000 | 1540000 | 1540000
| 1.1.2 | Site Assessment | 193963 | 294061 | 294061 | 294061
| 1.1.3 | Design and Engineering | 756926.3975 | 1619750.5558 | 3691598.0788 | 3508498.5912
|  | Total | 4553389.3975 | 8773811.5558 | 11003159.0788 | 10820059.5912
1.1.1.1 | Siting and Scoping |  |  | 1 Unit | 10 Units | 10-100 Units
|  | Resource Assessment |  | 90000 | 90000 | 90000
|  | Environmental Scoping |  | 75000 | 85000 | 85000
|  | Community Outreach |  | 65000 | 130000 | 130000
|  | Regulatory Outreach |  | 105000 | 120000 | 120000
|  | Sum |  | 335000 | 425000 | 425000
1.1.1.2 | Pre-Installation Studies |  |  | 1 Unit | 10 Units | 10-100 Units
|  | Detailed Resource Assessment - Hydrodynamic modeling |  | 0 | 140000 | 140000
|  | Seabed Survey & Mapping |  | 110000 | 110000 | 185000
|  | Marine Mammals |  | 552500 | 725000 | 617500
|  | Fish and Invertebrates |  | 617000 | 927000 | 682000
|  | Seabirds |  | 93500 | 158500 | 158500
|  | Turtles |  | 25000 | 90000 | 90000
|  | Water Quality |  | 47000 | 207000 | 207000
|  | Habitat |  | 20000 | 60000 | 247500
|  | Cultural Resources |  | 105000 | 120000 | 127500
|  | Navigation |  | 12500 | 12500 | 27500
|  | Recreation |  | 50000 | 300000 | 300000
|  | Sum |  | 1632500 | 2850000 | 2782500
1.1.1.3 | Post-Install Capital |  |  | 1 Unit | 10 Units | 10-100 Units
|  | Marine Mammals and Turtles |  | 237500 | 415000 | 415000
|  | Fish |  | 237500 | 415000 | 415000
|  | Seabirds |  | 112500 | 202500 | 202500
|  | Benthos |  | 80000 | 145000 | 145000
|  | Acoustic Characterization Monitoring |  | 42500 | 42500 | 42500
|  | Ecosystem Effects Seabird |  | 0 | 350000 | 350000
|  | Ecosystem Effects Marine Mammals & Turtles |  | 0 | 350000 | 350000
|  | Ecosystem Effects Fish |  | 0 | 350000 | 350000
|  | Sum |  | 710000 | 2270000 | 2270000
1.1.1.4 | NEPA and Process |  |  | 1 Unit | 10 Units | 10-100 Units
|  | NEPA Document Preparation |  | 800000 | 1100000 | 1325000
|  | Monitoring and Study Plans |  | 125000 | 215000 | 215000
|  | Sum |  | 925000 | 1315000 | 1540000
1.1.2 | Site Assessment |  |  | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Survey |  | 193963 | 294061 | 294061 | 294061
|  | Sum |  | 193963 | 294061 | 294061 | 294061
1.1.3 | Design & Engineering |  |  | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Installed Cost |  | 15138527.9497 | 53991685.1923 | 184579903.9397 | 350849859.115
|  | % of total assumpton |  | 5% | 3% | 2% | 1%
|  | Cost |  | 756926.3975 | 1619750.5558 | 3691598.0788 | 3508498.5912
Cost Estimating Notes
1.1.1 | Actual cost breakdowns are provided in separate report by PNNL (average values carried forward to this spreadsheet)
1.1.2 | - Bathimtric and Geophysical Survey
- Small site survey with dimensions of 3.5km x 1km one trunck cable corridor
- Large site survey with dimensions of 16.5km x 1km with trunck cable survey
- Includes: bathimetry, sub-bottom profiling, Magnetometer, Grab Samples, Underwater Video
1.1.3 | Design & Engineering is taken as a percentage of total hard cost of the device
Data Sources
1.1.1.1 | PNNL - Detailed in Separate Document
1.1.1.2 | PNNL - Detailed in Separate Document
1.1.1.3 | PNNL - Detailed in Separate Document
1.1.1.4 | PNNL - Detailed in Separate Document
1.1.2 | Estimate from survey company
1.1.3 | RE Vision Estimate

## 1.2
1.2 Infrastructure
Cost Summary |  |  | Units | 1 | 10 | 50 | 100
| 1.2.1 | Subsea Cables |  | 900000 | 900000 | 3360000 | 8700000
| 1.2.2 | Terminations and Connectors |  | 90000 | 90000 | 336000 | 870000
| 1.2.3 | Dockside Improvements |  | 0 | 0 | 0 | 0
| 1.2.4 | Dedicated O&M Vessel |  | 0 | 3870000 | 3870000 | 7740000
| 1.2.5 | Other
|  | Totals |  | 990000 | 4860000 | 7566000 | 17310000
1.2.1 Subsea Cables |  |  |  | # | Units
|  |  | 1 | 10 | 50 | 100
Capacity
|  | Unit Capacity (kW) | 350 | 350 | 350 | 350
|  | Plant Capacity (MW) | 0.35 | 3.5 | 17.5 | 35
|  | Target Cable Capacity incl. 20% contingency (MW) | 0.42 | 4.2 | 21 | 42
Determining Trunk-cable length, shore to first junction box
|  | Site Distance to shore | 5000 | 5000 | 5000 | 5000
|  | Array Cable | 0 | 0 | 9000 | 24000
|  | Contingency Cable Length incl. 20% Contingency (m) | 6000 | 6000 | 16800 | 34800
Inter-Device Cable Length
|  | Per Device Cable Length | 800 | 800 | 800 | 800
|  | Total Cable Length | 800 | 8000 | 40000 | 80000
Subsea Cable Cost
|  | Trunk Cable Cost ($/m) | 150 | 150 | 200 | 250
|  | Inter-Device Cable Cost (included in 1.5) | 0 | 0 | 0 | 0
Total Cost
|  | Trunck Cable | 900000 | 900000 | 3360000 | 8700000
|  | Inter-Device Cable | 0 | 0 | 0 | 0
|  | Total | 900000 | 900000 | 3360000 | 8700000
1.2.2 Terminations and Connectors
|  |  | 1-Unit | 10-Units | 50-Units | 100-Units
|  | 10% of Subsea Cable Cost | 90000 | 90000 | 336000 | 870000
|  | Cost | 90000 | 90000 | 336000 | 870000
1.2.3 Dockside Improvements
|  |  | 1-Unit | 10-Units | 50-Units | 100-Units
None
|  | Cost | 0 | 0 | 0 | 0
1.2.4 Dedicated O&M Vessel
|  |  | 1-Unit | 10-Units | 50-Units | 100-Units
Notes:
- Ship Conversion including: (1) DP-1, Crane, Whinch, Delivery etc.
- Using new vessel, values come in between $4.09M and $5.65M
- Using used vessel, values are estimated between $2.09M and $3.1M
|  | Vessel |  | 3870000 | 3870000 | 7740000
|  | Cost | 0 | 3870000 | 3870000 | 7740000
Cost Estimating Notes
| 1.2.1 | Rough Estimates were used for subsea cable cost
| 1.2.2 | Terminations and Connectors are difficult to estimate without a detailed design effort. Estimated them as 10% of Cable cost
| 1.2.3 | Not estimated, but included in project contingency
| 1.2.4 | See notes above
Data Sources
| 1.2.1 | RE Vision
| 1.2.2 | RE Vision
| 1.2.3 | RE Vision
| 1.2.4 | RE Vision

## 1.3
1.3 Mooring/Foundation
Cost Summary |  |  | Units | 1 | 10 | 50 | 100
| 1.3.1 | Mooring lines/chain |  | 182475 | 1642275 | 8211375 | 16422750
| 1.3.2 | Anchors |  | 180000 | 1620000 | 8100000 | 16200000
| 1.3.3 | Buoyancy |  | 60000 | 540000 | 2700000 | 5400000
| 1.3.3 | Connecting Hardware (shackles etc.) |  | 102300 | 920700 | 4603500 | 9207000
| 1.3.4 | Other
| Total |  |  | 524775 | 4722975 | 23614875 | 47229750
[5 empty] | # | Units
1.3.1 Mooring Lines / Chain |  |  |  | 1 | 10 | 50 | 100
| Wire Rope to Sub-Sea Buoys |  |  | 27000 | 243000 | 1215000 | 2430000
| Nylon Line 5.75" |  |  | 43875 | 394875 | 1974375 | 3948750
| Chain 3.5 inch, 90 foot shot |  |  | 111600 | 1004400 | 5022000 | 10044000
| Total |  |  | 182475 | 1642275 | 8211375 | 16422750
[5 empty] | # | Units
1.3.2 Anchors |  |  |  | 1 | 10 | 50 | 100
| Anchor - Bruce Mk-4, 9-tonne |  |  | 180000 | 1620000 | 8100000 | 16200000
| Total |  |  | 180000 | 1620000 | 8100000 | 16200000
[5 empty] | # | Units
1.3.3 Buoyancy |  |  |  | 1 | 10 | 50 | 100
| Sub-Sea Buoys (55kN net buoyancy) |  |  | 60000 | 540000 | 2700000 | 5400000
| Total |  |  | 60000 | 540000 | 2700000 | 5400000
[5 empty] | # | Units
1.3.4 Connecting Hardware |  |  |  | 1 | 10 | 50 | 100
| Anchor Joining Link |  |  | 14100 | 126900 | 634500 | 1269000
| Chain joining link |  |  | 14400 | 129600 | 648000 | 1296000
| Sinker (10-tonnes) |  |  | 27000 | 243000 | 1215000 | 2430000
| Shackles |  |  | 46800 | 421200 | 2106000 | 4212000
| Total |  |  | 102300 | 920700 | 4603500 | 9207000
Cost Estimating Notes
1.3.1 | Based on Preliminary Mooring Design
1.3.2 | Based on Preliminary Mooring Design
1.3.3 | Based on Preliminary Mooring Design
1.3.4 | Based on Preliminary Mooring Design
Data Sources
1.3.1 | RE Vision
1.3.2 | RE Vision
1.3.3 | RE Vision
1.3.4 | RE Vision

## 1.4
1.4 Device Structural Components
Cost Summary |  |  |  | 1 | 10 | 50 | 100 | Weight (tonnes)
| 1.4.1 |  | Surface Float | 894241.1454 | 6220786.6201 | 27374083.7994 | 53048701.149 | 205.44
| 1.4.2 |  | Vertical Column | 921357.2792 | 6544935.441 | 29155570.0724 | 56827841.0474 | 223.64
| 1.4.3 |  | Reaction Plate | 1065825.4675 | 7503582.0534 | 33223658.9095 | 64567902.9546 | 244.73
| 1.4.4 |  | Device Access (Railings, Ladders, etc) | 57628.4778 | 405386.0823 | 1795066.2556 | 3488888.903 | 13.4762
|  | Total |  | 2939052.3699 | 20674690.1967 | 91548379.0369 | 177933334.054 | 687.2862
1.4.1 | Surface Float
[5 empty] | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Material |  |  | 440328.2331 | 371343.6067 | 352262.5865 | 352262.5865
|  | Labor |  |  | 259506.7383 | 182871.2973 | 143185.7975 | 128867.2178
|  | Non-Reccuring |  |  | 113111.5244 | 11311.1524 | 2262.2305 | 1131.1152
|  | Profit |  |  | 81294.6496 | 56552.6056 | 49771.0615 | 48226.092
|  | Total |  |  | 894241.1454 | 622078.662 | 547481.676 | 530487.0115
|  | $/tonne |  |  | 4352.8093 | 3028.0309 | 2664.9225 | 2582.1992
|  | Mass |  | 205.44 | tonnes
1.4.2 | Vertical Column
[5 empty] | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Material |  |  | 504860.1453 | 425765.5384 | 403888.1163 | 403888.1163
|  | Labor |  |  | 224834.6972 | 158438.3242 | 124055.1041 | 111649.5937
|  | Non-Recurring |  |  | 107902.684 | 10790.2684 | 2158.0537 | 1079.0268
|  | Profit |  |  | 83759.7527 | 59499.4131 | 53010.1274 | 51661.6737
|  | Total |  |  | 921357.2792 | 654493.5441 | 583111.4014 | 568278.4105
|  | $/tonne |  |  | 4119.8233 | 2926.5496 | 2607.3663 | 2541.041
|  | Mass |  | 223.64 | tonnes
1.4.3 | Reaction Plate
[5 empty] | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Material |  |  | 554330.9167 | 467485.9035 | 443464.7333 | 443464.7333
|  | Labor |  |  | 286425.0204 | 201840.289 | 158038.2662 | 142234.4395
|  | Non-recurring |  |  | 128176.3061 | 12817.6306 | 2563.5261 | 1281.7631
|  | Profit |  |  | 96893.2243 | 68214.3823 | 60406.6526 | 58698.0936
|  | Total |  |  | 1065825.4675 | 750358.2053 | 664473.1782 | 645679.0295
|  | $/tonne |  |  | 4355.1075 | 3066.0655 | 2715.1276 | 2638.3322
|  | Mass |  | 244.73 | tonnes
1.4.4 | Device Access (Railings, Ladders, etc)
[5 empty] | 1-Unit | 10-Units | 50-Units | 100-Units
|  | Structural Cost Total from 1-3 |  |  | 2881423.8921 | 2026930.4114 | 1795066.2556 | 1744444.4515
|  | % of Structural |  |  | 2% | 2% | 2% | 2%
|  | Total |  |  | 57628.4778 | 40538.6082 | 35901.3251 | 34888.889
|  | $/tonne |  |  | 4276.3151 | 3008.1631 | 2664.054 | 2588.9263
|  | Unknown |  | 13.4762 | tonnes
Cost Estimating Notes
1.4.1 | Structural Design Details can be found in the main report, all costs are shown on a per unit basis, total costs are calculated in the summary
1.4.2 | Structural Design Details can be found in the main report, all costs are shown on a per unit basis, total costs are calculated in the summary
1.4.3 | Structural Design Details can be found in the main report, all costs are shown on a per unit basis, total costs are calculated in the summary
1.4.4 | Concept design did not allow to refine all design details. Used 2% of structural cost to account for ssmaller items such as device access, connecting elements etc.
Data Sources
1.4.1 | RE Vision Estimate
1.4.2 | RE Vision Estimate
1.4.3 | RE Vision Estimate
1.4.4 | RE Vision Estimate from similar experience

## 1.5
1.5 Power Take Off
Cost Summary |  |  |  | Single Unit in Mass Production | 1 | 10 | 50 | 100 | Prog Ratio | Mass (kg)
| 1.5.1 |  | Generator | 20037.16 | 25740 | 227101.823 | 1040339.5245 | 2003700 | 96.3% | 2073.5
| 1.5.2 |  | Hydraulic Components (all) | 95755.66 | 115140.74 | 1050019.8426 | 4922510.8914 | 9575600 | 97.26% | 7955.4603
| 1.5.3 |  | Hydraulic Energy Storage | 23452 | 56628 | 364422.8116 | 1338982.0596 | 2345200 | 87.57% | 1292.72
| 1.5.4 |  | Frequency Converter | 19305 | 85800 | 406985.1349 | 1208220.1022 | 1930500 | 79.89% | 1141.14
| 1.5.5 |  | Step-up Transformer | 42900 | 57200 | 495366.531 | 2239919.7042 | 4290000 | 95.76% | 0
| 1.5.6 |  | Riser Cable | 88000 | 88000 | 880000 | 4400000 | 8800000 | 100% | 0
| 1.5.7 |  | Electrical Energy Storage | 0 | 0 | 0 | 0 | 0 | 96.7% | 0
| 1.5.8 |  | Seals | 0 | 0 | 0 | 0 | 0 | 96.7% | 0
| 1.5.9 |  | Control System | 5000 | 5643.5 | 53120.1468 | 254597.342 | 500000 | 98.19% | 0
| 1.5.10 |  | Bearings and Linear Guides | 66307.956 | 88410.608 | 765658.579 | 3462111.4432 | 6630800 | 95.76% | 0
| 1.5.11 |  | Assembly, Testing & QA | 43500.6 | 58000.8 | 502303.9718 | 2271296.3216 | 4350100 | 95.76% | 0
| 1.5.12 |  | PTO mounting | 5720 | 28600 | 127903.0883 | 364394.2387 | 572000 | 78.49% | 0
| 1.5.13 |  | Other | 2860 | 14300 | 63951.5442 | 182197.1193 | 286000 | 78.49% | 0
|  |  | Total Cost |  | 623463.648 | 4936833.4731 | 21684568.7466 | 41283900 |  | 12462.8203
|  |  | Cost per unit | 412838.376 | 623463.648 | 493683.3473 | 433691.3749 | 412839
Single Unit Cost Breakdown for 100-kW baseline
|  |  | Component | Category | Cost - 100kW | Cost - 286kW |  | Mass - 100kW | Mass - 286kW
|  | 1 | Hydraulic Cylinder | Hydraulic Components (all) | 9350 | 26741 |  | 907.0295 | 2594.1043
|  | 2 | Check Valves | Hydraulic Components (all) | 408 | 1166.88 |  |  | 0
|  | 3 | Relieve Valves | Hydraulic Components (all) | 116 | 331.76 |  |  | 0
|  | 4 | Pressure Sensors | Control System | 225 | 643.5 |  |  | 0
|  | 5 | Solenoid Valves | Hydraulic Components (all) | 956 | 2734.16 |  |  | 0
|  | 6 | Valve Subplate | Hydraulic Components (all) | 702 | 2007.72 |  |  | 0
|  | 7 | Accumulator | Hydraulic Energy Storage | 19800 | 56628 |  | 452 | 1292.72
|  | 8 | HP Filter | Hydraulic Components (all) | 898 | 2568.28 |  | 50 | 143
|  | 9 | Return Filter | Hydraulic Components (all) | 2568 | 7344.48 |  | 90 | 257.4
|  | 10 | Fixed Displacement Motor | Hydraulic Components (all) | 8261 | 23626.46 |  | 73 | 208.78
|  | 11 | Reservoir | Hydraulic Components (all) | 7000 | 20020 |  | 454 | 1298.44
|  | 12 | Plumbing | Hydraulic Components (all) | 4000 | 11440 |  |  | 0
|  | 13 | Fluid | Hydraulic Components (all) | 6000 | 17160 |  | 1207.6 | 3453.736
|  | 14 | Misc | Other | 5000 | 14300 |  |  | 0
|  | 15 | Machine/Pipe Foundations | PTO mounting | 10000 | 28600 |  |  | 0
|  | 16 | Generator | Generator | 9000 | 25740 |  | 725 | 2073.5
|  | 17 | Frequency Converter | Frequency Converter | 30000 | 85800 |  | 399 | 1141.14
|  | 18 | Assembly & Testing | Assembly, Testing & QA | 20280 | 58000.8 |  |  | 0
|  | 19 | Step-up Transformer | Step-up Transformer | 20000 | 57200 |  | 760 | 2173.6
|  | 20 | Linear Guide | Bearings and Linear Guides | 30912.8 | 88410.608 |  |  | 0
|  | 21 | Riser Cable | Riser Cable | 88000 | 88000 |  |  | 0
|  | 22 | Control System | Control System | 5000 | 5000 |  |  | 0
|  | Sum |  |  | 154564 | 442053.04
100 Unit Cost Breakdown for 100kW baseline
|  |  | Component | Category | Cost - 100kW | Cost - 286kW |  | Mass - 100kW | Mass - 286kW
|  | 1 | Hydraulic Cylinder | Hydraulic Components (all) | 8500 | 24310 |  | 907.0295 | 2594.1043
|  | 2 | Check Valves | Hydraulic Components (all) | 328 | 938.08 |  |  | 0
|  | 3 | Relieve Valves | Hydraulic Components (all) | 97 | 277.42 |  |  | 0
|  | 4 | Pressure Sensors | Hydraulic Components (all) | 168 | 480.48 |  |  | 0
|  | 5 | Solenoid Valves | Hydraulic Components (all) | 758 | 2167.88 |  |  | 0
|  | 6 | Valve Subplate | Hydraulic Components (all) | 662 | 1893.32 |  |  | 0
|  | 7 | Accumulator | Hydraulic Energy Storage | 8200 | 23452 |  | 452 | 1292.72
|  | 8 | HP Filter | Hydraulic Components (all) | 846 | 2419.56 |  | 50 | 143
|  | 9 | Return Filter | Hydraulic Components (all) | 2417 | 6912.62 |  | 90 | 257.4
|  | 10 | Fixed Displacement Motor | Hydraulic Components (all) | 6255 | 17889.3 |  | 73 | 208.78
|  | 11 | Reservoir | Hydraulic Components (all) | 6500 | 18590 |  | 454 | 1298.44
|  | 12 | Plumbing | Hydraulic Components (all) | 2200 | 6292 |  |  | 0
|  | 13 | Fluid | Hydraulic Components (all) | 4750 | 13585 |  | 1207.6 | 3453.736
|  | 14 | Misc | Other | 1000 | 2860 |  |  | 0
|  | 15 | Machine/Pipe Foundations | PTO mounting | 2000 | 5720 |  |  | 0
|  | 16 | Generator | Generator | 7006 | 20037.16 |  | 725 | 2073.5
|  | 17 | Frequency Converter | Frequency Converter | 6750 | 19305 |  | 399 | 1141.14
|  | 18 | Assembly & Testing | Assembly, Testing & QA | 15210 | 43500.6 |  |  | 0
|  | 19 | Step-up Transformer | Step-up Transformer | 15000 | 42900 |  | 760 | 2173.6
|  | 20 | Linear Guide | Bearings and Linear Guides | 23184.6 | 66307.956 |  |  | 0
|  | 21 | Riser Cable | Riser Cable | 88000 | 88000 |  |  | 0
|  | 22 | Control System | Control System | 5000 | 5000 |  |  | 0
|  | Sum |  |  | 204831.6 | 412838.376
Cost Estimating Notes for Commercial Scale (100-Units)
- No design available for linear guides, estimated cost at 20% of PTO cost
- Costs have been estimated from a 100kW system design and scaled using the rated capacity of the RM3 device
Data Sources - Commercial Scale (100-Units)
| 1 | RE Vision Estimate
| 2 | RE Vision 100 KW Wave Power Hydraulic System Study
| 3 | RE Vision 100 KW Wave Power Hydraulic System Study
| 4 | RE Vision 100 KW Wave Power Hydraulic System Study
| 5 | RE Vision 100 KW Wave Power Hydraulic System Study
| 6 | RE Vision 100 KW Wave Power Hydraulic System Study
| 7 | RE Vision 100 KW Wave Power Hydraulic System Study
| 8 | RE Vision 100 KW Wave Power Hydraulic System Study
| 9 | RE Vision 100 KW Wave Power Hydraulic System Study
| 10 | RE Vision 100 KW Wave Power Hydraulic System Study
| 11 | RE Vision 100 KW Wave Power Hydraulic System Study
| 12 | RE Vision 100 KW Wave Power Hydraulic System Study
| 13 | RE Vision 100 KW Wave Power Hydraulic System Study
| 14 | RE Vision 100 KW Wave Power Hydraulic System Study
| 15 | RE Vision 100 KW Wave Power Hydraulic System Study
| 16 | RE Vision Estimate
| 17 | RE Vision Estimate
| 18 | RE Vision 100 KW Wave Power Hydraulic System Study
| 19 | RE Vision Estimate
| 20 | RE Vision Estimate
| 21 | RE Vision Estimate
| 22 | RE Vision Estimate
Cost Estimating Notes - Single Unit Scale
- Costs have been estimated from a 100kW system design and scaled using the rated capacity of the RM3 device
- No design available for linear guides, estimated cost at 20% of PTO cost
Data Sources - Single Unit Scale
| 1 | RE Vision 100 KW Wave Power Hydraulic System Study
| 2 | RE Vision 100 KW Wave Power Hydraulic System Study
| 3 | RE Vision 100 KW Wave Power Hydraulic System Study
| 4 | RE Vision 100 KW Wave Power Hydraulic System Study
| 5 | RE Vision 100 KW Wave Power Hydraulic System Study
| 6 | RE Vision 100 KW Wave Power Hydraulic System Study
| 7 | RE Vision 100 KW Wave Power Hydraulic System Study
| 8 | RE Vision 100 KW Wave Power Hydraulic System Study
| 9 | RE Vision 100 KW Wave Power Hydraulic System Study
| 10 | RE Vision 100 KW Wave Power Hydraulic System Study
| 11 | RE Vision 100 KW Wave Power Hydraulic System Study
| 12 | RE Vision 100 KW Wave Power Hydraulic System Study
| 13 | RE Vision 100 KW Wave Power Hydraulic System Study
| 14 | RE Vision 100 KW Wave Power Hydraulic System Study
| 15 | RE Vision 100 KW Wave Power Hydraulic System Study
| 16 | RE Vision Estimate
| 17 | RE Vision Estimate
| 18 | RE Vision 100 KW Wave Power Hydraulic System Study
| 19 | RE Vision Estimate
| 20 | RE Vision Estimate
| 21 | RE Vision Estimate
| 22 | RE Vision Estimate

## 1.6
1.6 Subsystem Integration and Profit Margin
|  |  | 1 | 10 | 50 | 100
|  | Machine Cost | 3562516.0179 | 25611523.6698 | 113232947.7836 | 219217234.0541
|  |  | 10% | 10% | 10% | 10%
|  | Totals | 356251.6018 | 2561152.367 | 11323294.7784 | 21921723.4054
|  |  | 10% of Machine Cost | 10% of Machine Cost | 10% of Machine Cost | 10% of Machine Cost
Cost Estimating Notes:
1.6 | Subsystem Integration and Profit margins are difficult to estimate given the level of design of the reference model. For consistency and to make it simple, this was assumed to be 10% of the machine cost. This is probably low for single unit production scale
However, because the primary focus of the RM effort is in identifying cost reduction pathways it was decided to apply this assumption, rather then an assumption as a function of deployment scale.
In reality, a figure closer to 30% is probably more realistic at single unit scale.
Data Sources
1.6 | RE Vision Assumption

## 1.7
1.7 Installation
Cost Summary
|  |  |  | Units | 1 | 10 | 50 | 100
| 1.7.1 |  | Transport to Staging Site |  | 29750 | 297500 | 1487500 | 2975000
| 1.7.2 |  | Cable Shore Landing |  | 667000 | 767200 | 767200 | 1534000
| 1.7.3 |  | Mooring/Foundation System |  | 3193833.55 | 3904558.5556 | 7063960.7778 | 11013213.5556
| 1.7.4 |  | Cable Installation |  | 1507533.78 | 2280164.6 | 4503814.6 | 7283377.1
| 1.7.5 |  | Device Installation |  | 255202.5 | 916275 | 3854375 | 7527000
| 1.7.6 |  | Device Comissioning |  | 255202.5 | 916275 | 3854375 | 7527000
| Total |  |  |  | 5908522.33 | 9081973.1556 | 21531225.3778 | 37859590.6556
[6 empty] | # | Units
1.7.1 | Transport Cost to Staging Site |  |  |  | 1 | 10 | 50 | 100
| Mooring Components |  |  |  | 29750 | 297500 | 1487500 | 2975000
Subsea Cable
| Total |  |  |  | 29750 | 297500 | 1487500 | 2975000
[6 empty] | # | Units
1.7.2 | Cable Landing |  |  |  | 1 | 10 | 50 | 100
Notes:
- Cost from previous projects in the Pacific Northwest
- Drilling Distance: 500m
- 1 Unit would require an 8" conduit
- 10 Units would require 10" Conduit
- 50 Units would require 1 x 10" conduit
- 100 Units would require 2 x 10" conduit
- Jettable Material < 7,500 psi
| Total HDD Activities |  |  |  | 667000 | 767200 | 767200 | 1534000
[6 empty] | # | Units
1.7.3 | Mooring Installation |  |  |  | 1 | 10 | 50 | 100
Notes:
- Mooring Installation Vessel M/V Mystique or similar
- Deck space = 5100 ft^2 => 2-3 moorings can be loaded
- Fuel at $3.5/gallon
[5 empty] | 1 Unit |  |  | 10 Units |  |  | 50 Units |  | 100 Units
|  |  |  | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost
| 1 | Transit (5000 miles) |  | 45.83 | 58754.2658 | 2692708 | 45.83 | 58754.2658 | 2692708 | 45.83 | 58754.2658 | 2692708 | 45.83 | 58754.2658 | 2692708
| 2 | Mob/Demob of Vessel |  | 4 |  | 422000 | 4 |  | 422000 | 4 |  | 422000 | 4 |  | 422000
| 3 | Dockside Support |  |  |  | 7350 |  |  | 73500 |  |  | 367500 |  |  | 735000
| 4 | At Dock Loading |  | 0.37 | 70485 | 26079.45 | 3.6667 | 70485 | 258445 | 18.3333 | 70485 | 1292225 | 36.6667 | 70485 | 2584450
| 5 | Transit to Site and back |  | 0.24 | 76610 | 18386.4 | 2.4444 | 76610 | 187268.8889 | 12.2222 | 76610 | 936344.4444 | 24.4444 | 76610 | 1872688.8889
| 6 | On-Site Working |  | 0.37 | 73810 | 27309.7 | 3.6667 | 73810 | 270636.6667 | 18.3333 | 73810 | 1353183.3333 | 36.6667 | 73810 | 2706366.6667
| Total |  |  | 50.81 |  | 3193833.55 | 59.6078 |  | 3904558.5556 | 98.7189 |  | 7063960.7778 | 147.6078 |  | 11013213.5556
1.7.4 | Cable Installation
Notes:
- Cable Installation Vessel
- Support Vessel
-Cable Installation and Burial Tools
Dayrates:
|  | At Dock Mob/Demob | 66350
|  | Loading Cable | 75625
|  | Transit | 101275
|  | Cable Lay Ops | 101075
|  | Standby | 87855 |  | 1 Unit |  |  | 1 0-Unit |  |  | 50 Unit |  |  | 100 Unit
|  |  |  | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost
Installation Process
|  | Mob/Demob CIV |  | 11 | 66350 | 729850 | 11 | 66350 | 729850 | 11 | 66350 | 729850 | 11 | 66350 | 729850
|  | Load Cable |  | 0.71 | 75625 | 53693.75 | 3.4 | 75625 | 257125 | 3.4 | 75625 | 257125 | 3.4 | 75625 | 257125
|  | Transit to Site |  | 2 | 101275 | 202550 | 2 | 101275 | 202550 | 2 | 101275 | 202550 | 2 | 101275 | 202550
|  | Install Cable & Surface Lay |  | 0.55 | 101075 | 55591.25 | 5.5 | 101075 | 555912.5 | 27.5 | 101075 | 2779562.5 | 55 | 101075 | 5559125
|  | Cable Burial and S/E |  | 3.1 | 101075 | 313332.5 | 3.1 | 101075 | 313332.5 | 3.1 | 101075 | 313332.5 | 3.1 | 101075 | 313332.5
Transit to/from Home Port
|  | Contingency | 10% | 1.736 | 87855 | 152516.28 | 2.52 | 87855 | 221394.6 | 2.52 | 87855 | 221394.6 | 2.52 | 87855 | 221394.6
| Total |  |  | 19.096 |  | 1507533.78 | 27.52 |  | 2280164.6 | 49.52 |  | 4503814.6 | 77.02 |  | 7283377.1
[6 empty] | # | Units
1.7.5 | Device Installation |  |  |  | 1 | 10 | 50 | 100
Notes:
- Installation continously until complete
- Workboat (the same as used for O&M)
- 2 tugs (800-1500 HP)
- Crew Boat
| - Shoreside support |  |  |  | 1 Unit |  |  | 10 Unit |  |  | 50 Unit |  |  | 100 Unit
|  |  |  | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost | # Days | Day-rate | Cost
Process
| 1 | Mob/Demob |  |  |  | 181750 |  |  | 181750 |  |  | 181750 |  |  | 181750
| 2 | Installation | 1 device per day | 1 | 66775 | 66775 | 10 | 66775 | 667750 | 50 | 66775 | 3338750 | 100 | 66775 | 6677500
| 3 | Contingency | 10% | 0.1 | 66775 | 6677.5 | 1 | 66775 | 66775 | 5 | 66775 | 333875 | 10 | 66775 | 667750
| Total |  |  | 1.1 |  | 255202.5 | 11 |  | 916275 | 55 |  | 3854375 | 110 |  | 7527000
1.7.6 | Device Comissioning |  |  |  | 1-Unit | 10-Units | 50-Units | 100-Units
Notes:
- Same setup as Device Installation
| Total |  |  |  | 255202.5 | 916275 | 3854375 | 7527000
Cost Estimating Notes
1.7.1
1.7.2 | See notes above in cost details
1.7.3 | See notes above in cost details
1.7.4 | See notes above in cost details
1.7.5 | See notes above in cost details
1.7.6 | See notes above in cost details
Data Sources
1.7.1 | RE Vision cost assessment
1.7.2 | RE Vision cost assessment
1.7.3 | RE Vision cost assessment
1.7.4 | RE Vision cost assessment
1.7.5 | RE Vision cost assessment
1.7.6 | RE Vision cost assessment

## 1.8
1.8 Decomissioning
Cost Estimating Notes
1.8 | Decomissioning costs are assumed to be the same as the installation costs, because similar operational procedures will be used to remove the plant hardware as for the installation process. The key difference is that decomissioning
occurs at the end of the 20-year project life, having a minimal impact on the cost of electricty from this plant. Decomissioning costs are not represented in the CoE assessment.
Data Sources
1.8 | RE Vision Esitmate

## 1.9
1.9 Contingency
Cost Estimating Notes
1.9 | Contingency captures unknown unknowns. Given the conceptual level of design, it is likely that quite a few items are not well understood and hence costs are under-predicted.
10% is used because that is what offshore wind has been using.
Data Sources
1.9 | RE Vision Estimae

## 2.1
2.1 Insurance
Cost Summary |  |  | Units | 1 | 10 | 50 | 100
| 2.1 | Insurance |  | 226841.299 | 936752.4838 | 1772683.4294 | 1717691.4906
|  | Percentage Rate |  | 2% | 2% | 1% | 0.5%
Assumptions
| 1 - Unit | 2% | Note: Typical in offshore one-off projects
| 10 - Units | 2%
| 50 - Units | 1%
| 100 - Units | 0.5% | Note: Typical in Onshore Wind, assuming high technical maturity
Cost Estimating Notes
2.1 | Insurance cost is a direct function of the perceived risk of a project. Offshore Oil & Gas project are typically on the order of 2% of CAPEX. These are one-off construction projects with a relatively high risk profile (oil-spill potential etc.).
On the other end of the spectrum is land-based wind that is technologically mature with typical insurance rates on the order of 0.5%. The assumption is that for 1 and 10-unit deployment scales technology is relatively immature
It is also assumed that no investor will take the risk of building a 100-unit farm unless technology risks are perceived as being really small.
Data Sources
2.1 | RE Vision Estimate based on related project experience

## 2.2
2.2 Environmental Monitoring and Regulatory Compliance
Cost Summary |  |  | 1 | 10 | 50 | 100
| 2.2 | Environmental Monitoring and Regulatory Compliance | 710000 | 1121000 | 1121000 | 1121000
Annualized Cost Breakdown |  |  | 1-Unit | 10 Units | 50-100 Units
|  | Marine Mammals and Turtles | 237500 | 237500 | 237500
|  | Fish | 237500 | 237500 | 237500
|  | Seabirds | 112500 | 112500 | 112500
|  | Benthos | 80000 | 80000 | 80000
|  | Acoustic Characterization Monitoring | 42500 | 42500 | 42500
|  | Incremental Cost for Farm Deployments |  | 411000 | 411000
|  | Total | 710000 | 1121000 | 1121000
Cost Estimating Notes
| 2.2 | Data directly taken from PNNL study
Data Sources
| 2.2 | PNNL - Described in Separate Report

## 2.3
2.3 Marine Operations
Cost Summary
|  |  |  | Units | 1 | 10 | 50 | 100
|  | 2.3 | Marine Operations |  | 26569 | 265690 | 562320 | 1124640
Vessel of Opportunity - 12-hour dayrates for Devicve Retrieval, Mooring Repair and Cable Repair
|  | Boat (incl. 4 person crew) | 8000
|  | Additional Crew | 3000
|  | Crew Boat | 3000
|  | Per Diem | 800
|  | Fuel and Consumables | 1500
|  | Total | 16300
Vessel of Opportunity - 12-hour dayrates for Device Access and PTO Swap-out
|  | Boat (incl. 4 person crew) | 8000
|  | Additional Crew | 3000
|  | Per Diem | 800
|  | Fuel and Consumables | 1000
|  | Total | 12800
Permanent Crew Dayrate
|  | Number of Crew | 10
|  | Average Hourly Rate | 30
|  | Hours/Day | 12
|  | Overhead | 30%
|  | Total Crew-day cost | 4680
|  | Fuel and Consumables | 1000
|  | Total | 5680
Failure Rates for Powertrain |  |  | # Failures / Year
Hydraulic System
|  | Cylinder | 0.13
|  | Fixed Displacement Motor | 0.2
|  | Generator | 0.1
|  | Frequency Converter | 0.13
|  | Step-up Transformer | 0.07
| Total |  | 0.63
# of Interventions per device-year Requiring Device Recovery
| Unscheduled Structural/Mooring/Riser Cable |  | 0.1
| Device Recovery for shore-side overhaul |  | 0.25
| Total |  | 0.35
|  |  | 1 Unit | 10 Units | 50 Units | 100 Units
| # of ops-days/year |  | 0.35 | 3.5 | 17.5 | 35
| $/day |  | 16300 | 16300 | 5680 | 5680
| $/year |  | 5705 | 57050 | 99400 | 198800
# of Interventions per device-year requiring PTO retrieval
| Rebuild Hydraulic System and Oil Change |  | 1
| Inspect Mooring System using ROV |  | 0.5
| # Hydraulic System Replacements/Ops-day |  | 2
| Unscheduled PTO repairs |  | 0.63
| Total |  | 1.63
|  |  | 1 Unit | 10 Units | 50 Units | 100 Units
| # of Ops days/year |  | 1.63 | 16.3 | 81.5 | 163
| $/day |  | 12800 | 12800 | 5680 | 5680
| $/year |  | 20864 | 208640 | 462920 | 925840
| Total Marine Ops Cost |  | 26569 | 265690 | 562320 | 1124640
Cost Estimating Notes
2.3 | Only critical components that can not be made redundant are considered in failure rate
Data Sources
2.3 | RE Vision

## 2.4
2.4 Shoreside Operations
Cost Summary |  |  | Units | 1 | 10 | 50 | 100
| 2.4 | Shoreside Operations |  | 141561 | 399936 | 454692 | 674634
Staffing Levels / Cost
|  | Salary ($/year) | Burden |  |  | # of Staff |  |  |  | Staffing Costs ($/Year) |  |  | Average | 100 Units | 50 Units | 10 Units | 1 Unit
|  | Wage ($/hr) | (%) | Total | years 1-5 | 6-10 | 11-15 | 16-20 | years 1-5 | 6-10 | 11-15 | 16-20
| Site Manager Salary | 85000 | 35 | 114750 | 1 | 1 | 1 | 1 | 114750 | 114750 | 114750 | 114750 | 114750 | 114750 | 114750 | 114750 | 0
| Admin. Asst. Salary | 35000 | 35 | 47250 | 2 | 2 | 2 | 2 | 94500 | 94500 | 94500 | 94500 | 94500 | 94500 | 47250 | 47250 | 23625
| Sr. Tech Wage | 18 | 35 | 24.3 | 1 | 2 | 3 | 4 | 50544 | 101088 | 151632 | 202176 | 126360 | 126360 | 63180 | 50544 | 50544
| Jr. Tech Wage | 12 | 35 | 16.2 | 4 | 6 | 7 | 9 | 134784 | 202176 | 235872 | 303264 | 219024 | 219024 | 109512 | 67392 | 67392
| Totals | [7 empty] | 394578 | 512514 | 596754 | 714690
[12 empty] | 554634 |  | 554634 | 334692 | 279936 | 141561
Additional Cost
| Dockside Rental | 60000
| Facilities Lease | 60000
| Total | 120000
Cost Estimating Notes
2.4 | Cost of shore-side ops is estimated based on Windpact O&M cost model provided by NREL (O&M Cost Estimator_revA_22Jun2006.xls). Below are the assumptions on labor and consumables. It is assumed that the labor associated with repair are similar to wind.
Data Sources
2.4 | WindPACT study from NREL operation and matinence model

## 2.5
2.5 Replacement Parts
# Units
Cost Summary |  |  |  | 1 | 10 | 50 | 100
| 2.5 | Replacement Parts |  | 53808.0733 | 491314.0141 | 2305303.0569 | 3920874.9
Failure Rates for 100kW Reference Powertrain
| Hydraulic System |  | $/Unit | # Units | L50 | $/Year | # Failures/Year | No redundancy
|  | Hydraulic Cylinder | 9350 | 1 | 8 | 1168.75 | 0.125 | 0.125
|  | Check Valves | 408 | 4 | 20 | 81.6 | 0.05
|  | Relief Valve | 116 | 1 | 5 | 23.2 | 0.2
|  | Pressure Sensor | 225 | 2 | 8 | 56.25 | 0.125
|  | Valve Subplate | 702 | 2
|  | Accumulator | 19800 | 4
|  | HP Filter | 898 | 1
|  | Return Filter | 2568 | 1
|  | Fixed Displacement Motor | 8261 | 1 | 5 | 1652.2 | 0.2 | 0.2
|  | Reservoir | 7000 | 1
Electrical Systems
|  | Generator | 7006 | 1 | 10 | 700.6 | 0.1 | 0.1
|  | Frequency Converter | 30000 | 1 | 7.5 | 4000 | 0.13333 | 0.13333
|  | Step-up Transformer | 20000 | 1 | 15 | 1333.3333 | 0.066667 | 0.066667
External Systems
|  | Riser Cable | 88000 | 1 | 10 | 8800 | 0.1
|  | Moorings | 524775 | 1 | 20 | 26238.75 | 0.05 | 0.05
|  | Linear Guides | 30514 | 1 | 10 | 3051.4 | 0.1
| Total |  |  |  |  | 47106.0833 | 1.25 | 0.675
Scaled Powertrain at Device Rated Capacity |  |  |  | 286 | kW
| Hydraulic System |  | $/Unit | # Units | L50 | $/Year | # Failures/Year | No redundancy
|  | Hydraulic Cylinder | 26741 | 1 | 8 | 3342.625 | 0.125 | 0.125
|  | Check Valves | 1166.88 | 4 | 20 | 233.376 | 0.05
|  | Relief Valve | 331.76 | 1 | 5 | 66.352 | 0.2
|  | Pressure Sensor | 643.5 | 2 | 8 | 160.875 | 0.125
|  | Valve Subplate | 2007.72 | 2
|  | Accumulator | 56628 | 4
|  | HP Filter | 2568.28 | 1
|  | Return Filter | 7344.48 | 1
|  | Fixed Displacement Motor | 23626.46 | 1 | 5 | 4725.292 | 0.2 | 0.2
|  | Reservoir | 20020 | 1
| Electrical Systems |  | 0
|  | Generator | 20037.16 | 1 | 10 | 2003.716 | 0.1 | 0.1
|  | Frequency Converter | 85800 | 1 | 7.5 | 11440 | 0.13333 | 0.13333
|  | Step-up Transformer | 57200 | 1 | 15 | 3813.3333 | 0.066667 | 0.066667
External Systems
|  | Riser Cable | 88000 | 1 | 10 | 8800 | 0.1
|  | Moorings | 524775 | 1 | 50 | 10495.5 | 0.02 | 0.02
|  | Linear Guides | 87270.04 | 1 | 10 | 8727.004 | 0.1
| Total |  |  |  |  | 53808.0733 | 1.22 | 0.645
Scaled Powertrain at Device Rated Capacity in Mass Production (100-Unit Scale)
| Hydraulic System |  | $/Unit | # Units | L50 | $/Year | # Failures/Year | No redundancy
|  | Hydraulic Cylinder | 24310 | 1 | 8 | 3038.75 | 0.125 | 0.125
|  | Check Valves | 938.08 | 4 | 20 | 187.616 | 0.05
|  | Relief Valve | 277.42 | 1 | 5 | 55.484 | 0.2
|  | Pressure Sensor | 480.48 | 2 | 8 | 120.12 | 0.125
|  | Valve Subplate | 1893.32 | 2
|  | Accumulator | 23452 | 4
|  | HP Filter | 2419.56 | 1
|  | Return Filter | 6912.62 | 1
|  | Fixed Displacement Motor | 17889.3 | 1 | 5 | 3577.86 | 0.2 | 0.2
|  | Reservoir | 18590 | 1
Electrical Systems
|  | Generator | 25740 | 1 | 10 | 2574 | 0.1 | 0.1
|  | Frequency Converter | 15027.87 | 1 | 7.5 | 2003.716 | 0.13333 | 0.13333
|  | Step-up Transformer | 42900 | 1 | 15 | 2860 | 0.066667 | 0.066667
External Systems
|  | Riser Cable | 88000 | 1 | 10 | 8800 | 0.1
|  | Moorings | 472297.5 | 1 | 50 | 9445.95 | 0.02 | 0.02
|  | Linear Guides | 65452.53 | 1 | 10 | 6545.253 | 0.1
| Total |  | 806580.68 |  |  | 39208.749 | 1.22 | 0.645
| $/kW-year |  | 137.0935
| Cost Progress Ratio |  | 97.3%
Cost at Different Unit Scales |  |  |  | # | Units
|  |  | 1 | 10 | 50 | 100
| Total |  | 53808.0733 | 49131.4014 | 46106.0611 | 39208.749
Cost Estimating Notes
2.5 | Mooring L50 life considers that a mooring repair results only in partial replacement
Data Sources
2.5 | RE Vision

## 2.6
2.6 Consumables
Cost Summary |  |  | Units | 1 | 10 | 50 | 100
| 2.6 | Consumables |  | 8000 | 80000 | 400000 | 800000
Consumables include |  |  | $/year-device
| Hydraulic Oil (replaced once per year) |  | 6000
| High Pressure Filter |  | 500
| Low Pressure Filter |  | 500
| Other |  | 1000
| Total |  | 8000
Cost Estimating Notes
2.6 | High level estimates based on similar projects
Data Sources
2.6 | RE Vision